## Sheet1
Fault 2021-12-22 19:37:09
| Fault Number | Building Trade | Trade Category | Type of Fault | Impact | Location | Cancel Status | Reported Date | Fault Acknowledged Date | Responded on Site Date | RA Conducted Date | Work Started Date | Work Completed Date | Action(s) Taken | Other Trades Required Date | Cost Cap Exceed Date | Assistance Requested Date | Fault Reference | End User Priority | Incident Report | Remarks
| FID4831 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-22 17:25:18 | 2021-12-22 17:28:31 | 2021-12-22 17:28:51 | 2021-12-22 17:29:11 | 2021-12-22 17:29:32 | 2021-12-22 17:30:13 | Adjusted the temperature setpoint from 28c to 20c and damper position from 100% auto to 0% manual in bms system make it cool | [6 empty] | Aircon make it cool-su-high
| FID4830 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2021-12-22 16:48:05 | [12 empty] | Need to open patient locker -Allan-low
| FID4827 | Mechanical | Lift & Escalators (Schindler) | Other: Lift door keep open and closeLift door keep open and close, for all levels | Whole Building | RMG > RH > All > Patient Lift 11 |  | 2021-12-22 15:46:21 | [12 empty] | Lift door keep open and close, for all levels -mani-low
| FID4825 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1059 |  | 2021-12-22 15:37:01 | 2021-12-22 15:42:04 | 2021-12-22 15:42:22 | 2021-12-22 15:42:40 | 2021-12-22 15:43:04 | 2021-12-22 15:47:48 | Adjusted vav 1-1-17 temperature setpoint from 20c to 24c in bms system make it warm. damper position automatically reduce from 90% open to 20%. | [6 empty] | Aircon too cold, make it warm-su-low
| FID4824 | Building | Door Knob / Handle | Unable to open or close properly | Localised to room | RMG > RSC > 8 > Children Centre Consult Rm 3 |  | 2021-12-22 15:35:14 | [12 empty] | Door handle loose-Allan-low
| FID4822 | Medical Equipment | Fridges & Freezers | Other: fridge got smell | Localised to room | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 7 |  | 2021-12-22 15:30:17 | 2021-12-22 17:16:51 | 2021-12-22 17:17:17 | 2021-12-22 17:18:36 | 2021-12-22 17:19:59 | 2021-12-22 17:21:09 | fridge smell clean retun back | [6 empty] | Fridge got smell-Aru-low
| FID4816 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 2 > Passenger Lift Lobby |  | 2021-12-22 14:22:29 | [12 empty] | Light fused-mani-low
| FID4815 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > Dental Clinic |  | 2021-12-22 14:21:43 | [12 empty] | Signage light bulb fused-mani-low
| FID4814 | Plumbing & Sanitary | Soap Dispenser | Other: Soap dispenser dropped | Localised to room | RMG > RH > 2 > Dental X-Ray |  | 2021-12-22 14:19:10 | [12 empty] | Soap dispenser dropped-Hossain-low
| FID4813 | Office and Furniture | Cabinet | Other: Screw loose | Localised to room | RMG > RH > 7 > CSSD |  | 2021-12-22 14:18:19 | 2021-12-22 14:53:12 | 2021-12-22 14:53:32 | 2021-12-22 14:53:52 | 2021-12-22 14:54:14 | 2021-12-22 14:54:47 | Yes done | [6 empty] | Cabinet screw loose -allan-low
| FID4811 | Building | Door Closer | Unable to open or close properly | Localised to room | RMG > RH > 8 > Delivery Suite 5 |  | 2021-12-22 13:30:33 | 2021-12-22 13:40:47 | 2021-12-22 13:41:08 | 2021-12-22 13:41:27 | 2021-12-22 13:41:47 | 2021-12-22 13:42:17 | Done already | [6 empty] | Door cannot stay open-allan-low
| FID4809 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 817 |  | 2021-12-22 13:28:11 | [12 empty] | Aircon make it warm-isyamudin-low
| FID4807 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 8 > Ward 855 |  | 2021-12-22 13:24:49 | [12 empty] | Wall clock not working-Hossain-low
| FID4802 | Electrical | Vending Machine | Other: Out of order | Affecting Public | RMG > RSC > 13 > Surgical Ctr |  | 2021-12-22 10:51:55 | [12 empty] | Coffee vending machine out of order-Hossain-low
| FID4801 | Electrical | Vending Machine | Unserviceable | Localised to room | RMG > RH > 7 > Corridor |  | 2021-12-22 10:50:54 | 2021-12-22 11:07:13 | 2021-12-22 11:07:44 | 2021-12-22 11:08:34 | 2021-12-22 11:09:04 | 2021-12-22 11:14:15 | Remove the cutlery box normal back | [6 empty] | Chef-in-a-box vending machine cutlery stuck-mani-low
| FID4800 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 7 > OT Clean Corridor |  | 2021-12-22 10:49:39 | 2021-12-22 11:22:09 | 2021-12-22 11:22:45 | 2021-12-22 11:24:37 | 2021-12-22 11:25:31 | 2021-12-22 11:37:43 | Replaced new bulb 2 nos | [6 empty] | Light flickering -mani-low
| FID4799 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2021-12-22 10:48:29 | 2021-12-22 11:18:16 | 2021-12-22 11:18:40 | 2021-12-22 11:19:02 | 2021-12-22 11:19:26 | 2021-12-22 11:20:06 | Done I have open | [6 empty] | Patient locker need to open -allan-low
| FID4797 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-22 10:35:24 | 2021-12-22 10:36:09 | 2021-12-22 10:36:34 | 2021-12-22 10:36:54 | 2021-12-22 10:37:13 | 2021-12-22 10:38:42 | delivered one Co2 cylinder | [6 empty] | Need one CO2 cylinder to be replaced- Shanmu-medium
| FID4791 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1337-1343 |  | 2021-12-22 09:31:35 | 2021-12-22 09:32:04 | 2021-12-22 09:32:28 | 2021-12-22 09:32:54 | 2021-12-22 09:33:35 | 2021-12-22 10:03:42 | Adjusted ahu setpoint temperature. | [6 empty] | Aircon make it cool-su-low
| FID4789 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 818 |  | 2021-12-22 09:07:51 | [12 empty] | Aircon very warm, make it cool-isyamudin-low
| FID4778 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 8 > Delivery Suite 6 |  | 2021-12-22 08:44:54 | 2021-12-22 08:51:40 | 2021-12-22 08:52:24 | 2021-12-22 08:53:01 | 2021-12-22 08:53:48 | 2021-12-22 09:08:45 | replaced new light bulb | [6 empty] | Light fused-a.bala-low
| FID4777 | Building | Door Frame | Misaligned / dangling | More than 1 room | RMG > RH > 9 > Business Centre Office 2 |  | 2021-12-22 08:40:56 | 2021-12-22 08:43:13 | 2021-12-22 08:43:38 | 2021-12-22 08:44:06 | 2021-12-22 08:44:57 | 2021-12-22 08:45:52 | door closer screw adjusted | [6 empty] | Door hinge loose-v.bala-low
| FID4776 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 2 > Dental Clinic |  | 2021-12-22 08:37:51 | [12 empty] | Light fused -senthil-low
| FID4775 | Plumbing & Sanitary | Urinal | Choked | More than 1 room | RMG > RSC > 2 > Male Toilet |  | 2021-12-22 08:28:39 | [12 empty] | Urinal choke-Allan-low
| FID4772 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 8 > Ward 854 |  | 2021-12-22 01:13:52 | 2021-12-22 01:14:31 | 2021-12-22 01:15:09 | 2021-12-22 01:15:31 | 2021-12-22 01:15:46 | 2021-12-22 01:17:47 | adjusted the aircon temprature make it cold | [6 empty] | Aircon make it cold-a.bala-low
| FID4771 | Mechanical | AHU / FCU / CU | Misaligned / dangling | More than 1 room | RMG > RH > 10 > Stn D Corridor |  | 2021-12-22 00:36:43 | 2021-12-22 00:38:27 | 2021-12-22 00:38:58 | 2021-12-22 00:39:20 | 2021-12-22 00:39:52 | 2021-12-22 00:40:28 | fixed back | [6 empty] | Diffuser dropped-v.bala-low
| FID4770 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 9 > Corridor |  | 2021-12-21 22:24:35 | 2021-12-21 22:29:03 | 2021-12-21 22:29:56 | 2021-12-21 22:30:25 | 2021-12-21 22:30:49 | 2021-12-21 22:32:02 | replaced new light bulb | [6 empty] | Light fused -a.bala-low
| FID4769 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-21 19:36:28 | [12 empty] | Need one big co2 cylinder-nazri-medium
| FID4768 | Plumbing & Sanitary | Water Heater | Damaged / Loose / Cracked | Localised to room | RMG > RH > 7 > OT Tea Rm |  | 2021-12-21 19:33:50 | 2021-12-21 19:37:41 | 2021-12-21 19:45:06 | 2021-12-21 19:45:51 | 2021-12-21 19:46:47 | 2021-12-21 19:47:45 | replace new tap no more leaking | [6 empty] | Water dispenser hot water leaking-satha-low
| FID4765 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 12 > Rehab Con Rm 3 |  | 2021-12-21 16:52:05 | [12 empty] | Aircon make it cool-ilayaraja-low
| FID4763 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 818 |  | 2021-12-21 16:48:55 | 2021-12-21 16:54:32 | 2021-12-21 16:55:10 | 2021-12-21 17:02:23 | 2021-12-21 17:05:28 | 2021-12-21 17:06:59 | adjusted the thermostat not working . close diffuser for 70 percent . | [6 empty] | Aircon make it cool-aru-low
| FID4762 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-21 16:47:57 | 2021-12-21 17:02:23 | 2021-12-21 17:02:53 | 2021-12-21 17:04:43 | 2021-12-21 17:13:59 | 2021-12-21 17:15:22 | replaced the new cylinder | [6 empty] | Need to replace 1 big CO2 cylinder-ilayaraja-medium
| FID4761 | Medical Equipment | Fridges & Freezers | Other: Fridge not cold | Localised to room | RMG > RH > 8 > Nursing Stn B |  | 2021-12-21 16:43:23 | 2021-12-21 16:56:07 | 2021-12-21 16:56:33 | 2021-12-21 16:56:58 | 2021-12-21 16:57:55 | 2021-12-21 16:59:19 | replace battery | [6 empty] | Medication fridge showing low and not cold-satha-low
| FID4760 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 12 > Rehab Con Rm 2 |  | 2021-12-21 16:38:14 | 2021-12-21 16:45:16 | 2021-12-21 16:45:46 | 2021-12-21 16:46:10 | 2021-12-21 16:46:32 | 2021-12-21 17:28:40 | Adjusted vav 12-1-6 temperature setpoint from 21c to 19c and damper position from auto (38%) to 60% manual in bms system make it cool | [6 empty] | Aircon make it cool-su-low
| FID4759 | Building | Door Stopper | Other: Door unable to stay open | Localised to room | RMG > RSC > 12 > Rehab Con Rm 2 |  | 2021-12-21 16:36:52 | [12 empty] | Door unable to stay open -ming cai-low
| FID4758 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 1 > A&E |  | 2021-12-21 16:35:48 | [12 empty] | Aircon make it cool-isyamudin-low
| FID4757 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 6 |  | 2021-12-21 16:05:55 | 2021-12-21 16:06:21 | 2021-12-21 16:06:39 | 2021-12-21 16:06:57 | 2021-12-21 16:07:16 | 2021-12-21 16:09:55 | Adjusted the temperature setpoint from 16c to 14c and heater to 0% manual in bms system make it cooler | [6 empty] | Aircon make it cool-su-low
| FID4755 | Electrical | Light Bulb | Other: Different colour | Affecting Public | RMG > RH > All > Passenger Lift 6 |  | 2021-12-21 15:49:27 | [12 empty] | Need to replace the light in VL6, different colour -senthil-low
| FID4754 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Affecting Public | RMG > RH > 9 > Ward 960 - 961 |  | 2021-12-21 15:42:56 | 2021-12-21 16:04:29 | 2021-12-21 16:05:37 | 2021-12-21 16:06:14 | 2021-12-21 16:14:46 | 2021-12-21 16:20:22 | replaced the new hose & spray | [6 empty] | Bidet spray faulty-ilayaraja-low
| FID4753 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 1 > A&E |  | 2021-12-21 15:41:57 | 2021-12-21 15:43:28 | 2021-12-21 15:43:48 | 2021-12-21 15:44:07 | 2021-12-21 15:44:27 | 2021-12-21 15:50:19 | Adjusted FCU 1-10-1 cooling valve from 40% to 50% in bms system make it cool. Temperature setpoint is 23c | [6 empty] | Aircon make it cool-su-low
| FID4752 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 9 > Corridor |  | 2021-12-21 15:10:21 | 2021-12-21 15:31:38 | 2021-12-21 15:31:58 | 2021-12-21 15:32:22 | 2021-12-21 15:32:43 | 2021-12-21 15:33:16 | Bulb change done | [6 empty] | Light fused-allan-low
| FID4750 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-21 14:45:14 | 2021-12-21 14:49:10 | 2021-12-21 14:49:30 | 2021-12-21 14:49:51 | 2021-12-21 15:04:05 | 2021-12-21 15:11:29 | Adjusted the temperature setpoint from 28c to 20c and heater from auto (100%) to 0% manual in bms system make it cool | [6 empty] | Aircon make it cool-su-low
| FID4749 | Medical Equipment | Fridges & Freezers | Other: Fridge not cold | Localised to room | RMG > RH > 8 > Nursing Stn B |  | 2021-12-21 14:43:13 | 2021-12-21 14:43:57 | 2021-12-21 14:44:28 | 2021-12-21 14:44:52 | 2021-12-21 14:46:00 | 2021-12-21 14:52:00 | clear the ice reduce the setpoint checked compressor running normal | [6 empty] | Medication fridge showing low and not cold-satha-low
| FID4744 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-21 13:55:38 | [12 empty] | Aircon make it cool-isyamudin-low
| FID4743 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 1 > Nuclear Med Office |  | 2021-12-21 13:54:47 | 2021-12-21 13:56:33 | 2021-12-21 13:56:53 | 2021-12-21 13:57:13 | 2021-12-21 13:57:33 | 2021-12-21 13:59:43 | Adjusted AHU 1-5 temperature setpoint from 22.5c to 22c in bms system make it cool. Cooling valve increased from 63% to 73%. | [6 empty] | Aircon make it cool-su-low
| FID4739 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 13 > Ward 1337-1343 Nurse Station |  | 2021-12-21 13:08:04 | 2021-12-21 13:26:37 | 2021-12-21 13:26:57 | 2021-12-21 13:27:18 | 2021-12-21 13:27:40 | 2021-12-21 13:28:16 | Change battery | [6 empty] | Need to replace wall clock battery-allan-low
| FID4738 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 13 > Ward 1328-1336 Nurse Station |  | 2021-12-21 13:06:59 | 2021-12-21 13:29:13 | 2021-12-21 13:29:40 | 2021-12-21 13:30:04 | 2021-12-21 13:30:29 | 2021-12-21 13:31:17 | Change battery done | [6 empty] | Need to replace wall clock battery-allan-low
| FID4736 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > RIPC Waiting Area |  | 2021-12-21 12:23:52 | [12 empty] | Need to change the ceiling light-Nazri-low
| FID4732 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 1 > Level 1 |  | 2021-12-21 11:32:47 | 2021-12-21 11:39:21 | 2021-12-21 11:42:35 | 2021-12-21 11:43:17 | 2021-12-21 11:43:39 | 2021-12-21 11:45:24 | Delivered 5 nos O2 cylinders to facilities | [6 empty] | Need to send 5 takeo oxygen cylinders for CC-shanmu-low
| FID4731 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 8 > Ward 812 |  | 2021-12-21 11:25:27 | [12 empty] | Need to replace new wall clock battery-nazri-low
| FID4727 | Plumbing & Sanitary | Urinal | Choked | Affecting Public | RMG > RSC > 2 > Male Toilet |  | 2021-12-21 09:55:28 | 2021-12-21 11:28:30 | 2021-12-21 11:29:02 | 2021-12-21 11:30:01 | 2021-12-21 11:30:56 | 2021-12-21 11:32:01 | cleared the chock | [6 empty] | Urinal choke-ilayaraja-low
| FID4717 | Office and Furniture | Patient Bed | Cannot operate / defective | Localised to room | RMG > RH > 9 > Ward 973 - 975 |  | 2021-12-21 09:27:12 | 2021-12-21 11:36:28 | 2021-12-21 11:37:03 | 2021-12-21 11:37:39 | 2021-12-21 11:39:24 | 2021-12-21 11:40:55 | reset the power then back to normal | [6 empty] | Bed not working-ilayaraja-low
| FID4708 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-21 08:57:28 | 2021-12-21 09:16:59 | 2021-12-21 09:17:35 | 2021-12-21 09:18:07 | 2021-12-21 09:20:56 | 2021-12-21 09:26:58 | adjusted temperature in 23 degree | [6 empty] | Aircon too cold, make it warm-V.bala-low
| FID4707 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 13 > Ward 1328-1336 Nurse Station |  | 2021-12-21 08:26:49 | 2021-12-21 10:06:45 | 2021-12-21 10:07:18 | 2021-12-21 10:08:08 | 2021-12-21 10:08:47 | 2021-12-21 10:09:42 | battery chain | [6 empty] | Need to replace wall clock battery-alan-low
| FID4706 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn C |  | 2021-12-21 08:06:54 | 2021-12-21 08:15:18 | 2021-12-21 08:15:47 | 2021-12-21 08:16:18 | 2021-12-21 08:18:20 | 2021-12-21 08:22:10 | adjusted vav control in bms setpoint 24to22 make it cool | [6 empty] | Aircon too warm-v.bala-low
| FID4705 | Office and Furniture | Telephone | Cannot operate / defective | Localised to room | RMG > RH > 9 > Ward 919 |  | 2021-12-21 08:02:43 | [12 empty] | Telephone not working-v.bala-low
| FID4704 | Electrical | Light Bulb | Tripped / Short-Circuit / Overloaded | Localised to room | RMG > RH > 7 > Day Surgery Corridor |  | 2021-12-21 07:58:58 | 2021-12-21 08:53:26 | 2021-12-21 08:55:01 | 2021-12-21 09:21:08 | 2021-12-21 09:21:49 | 2021-12-21 09:23:02 | replaced new light bulb | [6 empty] | Lights trip-abala-high
| FID4703 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 9 > Ward 978 - 979 |  | 2021-12-21 07:51:33 | 2021-12-21 08:46:48 | 2021-12-21 08:47:24 | 2021-12-21 08:47:52 | 2021-12-21 08:48:28 | 2021-12-21 08:49:22 | replaced new light bulb | [6 empty] | Call bell keep ringing-abala-low
| FID4702 | Building | Filter | Dirty / Odour | Localised to room | RMG > RH > 7 > CSSD |  | 2021-12-21 07:37:12 | 2021-12-21 07:38:04 | 2021-12-21 07:38:27 | 2021-12-21 07:38:48 | 2021-12-21 07:39:35 | 2021-12-21 07:40:10 | replaced new filter | [6 empty] | Need to change new filter-v.bala-low
| FID4701 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-21 00:42:36 | 2021-12-21 00:43:49 | 2021-12-21 00:44:20 | 2021-12-21 00:44:44 | 2021-12-21 00:46:56 | 2021-12-21 00:47:40 | adjusted vav control in bms setpoint 20to24 make it warm | [6 empty] | Aircon too cold, make it warm-v.bala-low
| FID4699 | Mechanical | BMS / BAS | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-20 18:51:10 | 2021-12-20 18:52:34 | 2021-12-20 18:52:57 | 2021-12-20 18:53:26 | 2021-12-20 18:53:52 | 2021-12-20 18:55:49 | temprature setpoint at 26 degree heater manully 0 % change to auto 100 % | [6 empty] | Aircon make it warm to 24, aircon too cool-satha-low
| FID4698 | Mechanical | AHU / FCU / CU | Leaking / Condensation | Affecting Public | RMG > RSC > 1 > Visitor Lift Lobby |  | 2021-12-20 18:42:36 | 2021-12-20 18:43:05 | 2021-12-20 18:43:27 | 2021-12-20 18:43:51 | 2021-12-20 18:45:24 | 2021-12-20 18:46:13 | vaccume drain pipe and clear the choke | [6 empty] | Water leaking from the ceiling aircon-satha-low
| FID4695 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 12 > Raffles Health Screeners |  | 2021-12-20 17:57:02 | 2021-12-20 18:14:55 | 2021-12-20 18:15:23 | 2021-12-20 18:15:44 | 2021-12-20 18:16:10 | 2021-12-20 18:16:36 | clear | [6 empty] | Basin choke-ming cai-low
| FID4694 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-20 17:48:00 | 2021-12-20 17:48:44 | 2021-12-20 17:49:11 | 2021-12-20 17:49:39 | 2021-12-20 17:50:23 | 2021-12-20 17:57:32 | adjusted setpoint to 22 degree in bms | [6 empty] | Aircon make it cool-satha-low
| FID4692 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 11 > MRO |  | 2021-12-20 16:58:31 | 2021-12-21 13:33:45 | 2021-12-21 13:34:07 | 2021-12-21 13:34:29 | 2021-12-21 13:35:05 | 2021-12-21 13:35:44 | Bulb change done | [6 empty] | Need to change the ceiling light-Allan-low
| FID4689 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 8 > Delivery Suite 3 |  | 2021-12-20 15:58:56 | 2021-12-20 16:01:50 | 2021-12-20 16:02:53 | 2021-12-20 16:05:25 | 2021-12-20 16:05:44 | 2021-12-20 16:06:21 | Adjust setpoint temperature. | [6 empty] | Aircon need to make cool-Isyamudin-low
| FID4688 | Mechanical | Mechanical Ventilation | Cannot Open or Close | More than 1 room | RMG > RH > 9 > Ward 973 - 975 |  | 2021-12-20 15:28:17 | [12 empty] | Bed cannot adjust up and down -ming cai-low
| FID4686 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 7 > Histo Data Rm |  | 2021-12-20 15:04:05 | 2021-12-21 13:36:44 | 2021-12-21 13:37:05 | 2021-12-21 13:37:28 | 2021-12-21 13:37:56 | 2021-12-21 13:38:26 | Bulb change done | [6 empty] | Need to replace the ceiling light-Allan-low
| FID4685 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1065 |  | 2021-12-20 14:58:51 | 2021-12-20 15:06:51 | 2021-12-20 15:07:28 | 2021-12-20 15:10:44 | 2021-12-20 15:13:23 | 2021-12-20 15:15:43 | adjested the setpoint & airflow from bms | [6 empty] | Aircon very cool, make it warm - ilayaraja-low
| FID4680 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 7 > Day Surgery Rm 13 |  | 2021-12-20 12:49:38 | 2021-12-20 14:29:33 | 2021-12-20 14:29:52 | 2021-12-20 14:30:12 | 2021-12-20 14:30:53 | 2021-12-20 14:32:12 | clear the chock | [6 empty] | Basin choke -ming cai-low
| FID4677 | Office and Furniture | Cabinet | Cannot open / close | Affecting Public | RMG > RH > 2 > Dental Surgery 3 |  | 2021-12-20 11:45:39 | 2021-12-20 16:57:27 | 2021-12-20 16:57:51 | 2021-12-20 16:58:10 | 2021-12-20 16:58:39 | 2021-12-20 16:59:15 | open the door | [6 empty] | Drawer stuck-ming cai-low
| FID4675 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 1 > Nuclear Medicine Centre |  | 2021-12-20 11:44:28 | 2021-12-20 11:57:21 | 2021-12-20 11:58:16 | 2021-12-20 12:03:03 | 2021-12-20 12:04:43 | 2021-12-20 12:06:23 | replaced the new oxigen cylinder | [6 empty] | Need to change 1 small oxygen cylinder for e-trolley-ilayaraja-medium
| FID4671 | Plumbing & Sanitary | Soap Dispenser | Other: Relocation | Localised to room | RMG > RH > 1 > Unit #01-11 Retail Phamacy |  | 2021-12-20 11:01:00 | 2021-12-20 11:12:31 | 2021-12-20 11:12:52 | 2021-12-20 11:13:16 | 2021-12-20 11:28:45 | 2021-12-20 11:30:28 | Move to the opposite side | [6 empty] | Need to relocate hand towel dispenser -ming cai-low
| FID4670 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1052 |  | 2021-12-20 10:53:58 | 2021-12-20 11:43:13 | 2021-12-20 11:43:42 | 2021-12-20 11:44:46 | 2021-12-20 11:45:37 | 2021-12-20 11:47:24 | adjusted the setpoint temperature to 24 degrees and position at 20 % opening .checked on site | [6 empty] | Aircon make it warm -satha-low
| FID4668 | Mechanical | Fire Extinguisher | Misaligned / dangling | Localised to room | RMG > RH > 11 > Bed Lift Lobby |  | 2021-12-20 10:20:48 | 2021-12-20 11:49:47 | 2021-12-20 11:50:27 | 2021-12-20 11:50:34 | 2021-12-20 11:50:40 | 2021-12-20 11:53:32 | fixed back | [6 empty] | Fire extinguisher dropped-Shanmu-low
| FID4667 | Mechanical | Auto Sliding Glass Door | Misaligned / dangling | Localised to room | RMG > RSC > 11 > Fireman Lift Lobby |  | 2021-12-20 10:18:44 | 2021-12-20 10:25:04 | 2021-12-20 10:50:32 | 2021-12-20 10:52:58 | 2021-12-20 12:53:23 | [8 empty] | Need to check alignment of the EM door, EM lock not touching-ilayaraja-low
| FID4666 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | Localised to room | RMG > RH > 12 > RHS Male Toilet |  | 2021-12-20 10:14:42 | 2021-12-20 10:25:52 | 2021-12-20 10:47:22 | 2021-12-20 10:47:52 | 2021-12-20 10:48:17 | 2021-12-20 10:48:46 | Cleared the choke | [6 empty] | Toilet bowl choke-Allan-low
| FID4665 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 11 > MRO |  | 2021-12-20 10:12:33 | [12 empty] | Light fused-Senthil-low
| FID4664 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 11 > Room 1115 (CTU) |  | 2021-12-20 10:11:37 | [12 empty] | Light fused-Senthil-low
| FID4660 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RSC > 9 > Internal Med |  | 2021-12-20 09:22:34 | 2021-12-20 11:50:27 | 2021-12-20 11:50:49 | 2021-12-20 11:51:28 | 2021-12-20 11:51:58 | 2021-12-20 11:54:51 | ddc failed restart back normal | [6 empty] | Aircon very warm -satha-low
| FID4652 | Mechanical | Lift & Escalators | System Shows fault / Error code | Localised to room | RMG > RSC > B1 > B1 |  | 2021-12-20 08:46:35 | 2021-12-20 08:52:38 | 2021-12-20 08:53:24 | 2021-12-20 08:53:49 | 2021-12-20 08:54:28 | 2021-12-20 08:57:52 | Reset normal back | [6 empty] | Escalator 05 not running, error code '4' -mani-low
| FID4651 | Medical Equipment | Mortuary Fridge & Freezers | Alarm | Localised to room | RMG > RSC > 11 > Radiology |  | 2021-12-20 08:42:02 | 2021-12-20 10:44:37 | 2021-12-20 10:45:01 | 2021-12-20 10:45:26 | 2021-12-20 10:46:05 | 2021-12-20 10:46:36 | Replaced new battery for testo data logger | [6 empty] | Testo data logger not working -aru-low
| FID4649 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-20 08:33:07 | 2021-12-20 10:41:28 | 2021-12-20 10:41:54 | 2021-12-20 10:42:18 | 2021-12-20 10:43:02 | 2021-12-20 10:43:38 | Adjusted the aircon temperature in bms system make it cool | [6 empty] | Aircon make it cool -aru-low
| FID4648 | Office and Furniture | TV | Cannot open / close | Localised to room | RMG > RH > 7 > Call Centre |  | 2021-12-20 08:12:39 | 2021-12-20 08:12:59 | 2021-12-20 08:13:19 | 2021-12-20 08:13:44 | 2021-12-20 08:14:05 | 2021-12-20 08:17:09 | Replaced new battery | [6 empty] | TV remote not working -mani -low
| FID4647 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 1 > A&E |  | 2021-12-20 08:07:31 | 2021-12-20 10:38:26 | 2021-12-20 10:38:51 | 2021-12-20 10:39:14 | 2021-12-20 10:40:17 | 2021-12-20 10:40:55 | Replaced new oxygen cylinder | [6 empty] | Need to replace 2 big oxygen cylinder -aru-medium
| FID4645 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > A&E Waiting Area |  | 2021-12-20 07:38:27 | 2021-12-20 07:38:49 | 2021-12-20 07:39:32 | 2021-12-20 07:39:57 | 2021-12-20 07:40:26 | 2021-12-20 07:44:23 | Replaced new bulb | [6 empty] | Need to change bulb -mani-low
| FID4644 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 1 > A&E Bed 1 & 2 |  | 2021-12-20 07:30:18 | 2021-12-20 07:30:51 | 2021-12-20 07:31:22 | 2021-12-20 07:31:58 | 2021-12-20 07:32:17 | 2021-12-20 07:35:24 | call bell Reset normal back | [6 empty] | Call bell not ringing-mani-low
| FID4639 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1065 |  | 2021-12-19 18:29:02 | 2021-12-19 18:30:10 | 2021-12-19 18:30:54 | 2021-12-19 18:32:05 | 2021-12-19 18:34:08 | 2021-12-19 18:36:09 | Bms adjuted the aircon temprature make it warm | [6 empty] | Aircon make it warm-a.bala-low
| FID4637 | Plumbing & Sanitary | Basin / sink | Choked | More than 1 room | RMG > RH > 10 > Ward 1061 |  | 2021-12-19 18:13:36 | 2021-12-19 18:20:59 | 2021-12-19 18:22:49 | 2021-12-19 18:23:18 | 2021-12-19 18:24:29 | 2021-12-19 18:25:49 | basin choke cleared | [6 empty] | Basin choke-v.bala-low
| FID4635 | Mechanical | Pneumatic Tube | System Shows fault / Error code | More than 1 room | RMG > RH > 2 > RM@RH Counter |  | 2021-12-19 17:03:06 | 2021-12-19 17:04:11 | 2021-12-19 17:04:38 | 2021-12-19 17:05:02 | 2021-12-19 17:05:26 | 2021-12-19 17:07:52 | working normal test to send tube and recived back | [6 empty] | Pneumatic tube system not working-satha-low
| FID4633 | Office and Furniture | Chair | Cannot operate / defective | More than 1 room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-19 16:38:37 | 2021-12-19 17:33:31 | 2021-12-19 17:34:00 | 2021-12-19 17:34:42 | 2021-12-19 17:35:52 | 2021-12-19 17:38:32 | screw missing replaced new screw | [6 empty] | Need to tighten screw-v.bala-low
| FID4632 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Nursing Stn C |  | 2021-12-19 16:15:01 | 2021-12-19 16:42:13 | 2021-12-19 16:42:39 | 2021-12-19 16:43:21 | 2021-12-19 17:39:37 | 2021-12-19 17:43:34 | adjusted vav control in bms aircon make it cool | [6 empty] | Aircon make it cool-v.bala-low
| FID4631 | Building | Door Frame | Noisy | More than 1 room | RMG > RH > 8 > Ward 850 |  | 2021-12-19 14:30:40 | 2021-12-19 16:05:17 | 2021-12-19 16:05:45 | 2021-12-19 16:06:10 | 2021-12-19 16:08:26 | 2021-12-19 16:10:00 | door closer screw loose tighten back normal | [6 empty] | Door very noisy-v.bala-low
| FID4627 | Office and Furniture | Safe Box | Cannot open / close | More than 1 room | RMG > RH > 13 > Ward 1328-1336 |  | 2021-12-19 11:57:43 | 2021-12-19 13:41:53 | 2021-12-19 13:42:44 | 2021-12-19 13:43:10 | 2021-12-19 13:43:42 | 2021-12-19 13:44:37 | number locker cannot open master key use | [6 empty] | Patient locker need to open-v.bala-low
| FID4625 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 13 |  | 2021-12-19 09:41:36 | 2021-12-20 10:50:43 | 2021-12-20 10:51:06 | 2021-12-20 10:51:32 | 2021-12-20 10:51:55 | 2021-12-20 10:52:39 | Manually adjust the cooling valve onsite to make the aircon warm | [6 empty] | Aircon too cold, make it warm-isyamudin-low
| FID4620 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 13 |  | 2021-12-19 03:41:44 | 2021-12-19 04:01:14 | 2021-12-19 04:01:43 | 2021-12-19 04:03:29 | 2021-12-19 04:05:06 | 2021-12-19 04:06:33 | setpoint adjust 24to 26 aircon make it warm | [6 empty] | Aircon make it warm-aru-low
| FID4619 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1328-1336 |  | 2021-12-19 03:29:28 | 2021-12-19 03:30:06 | 2021-12-19 03:30:34 | 2021-12-19 03:31:31 | 2021-12-19 03:31:57 | 2021-12-19 03:37:29 | adjusted the aircon temperature from 20c to 25c and damber from auto to 20% manual in bms system make it warm | [6 empty] | Aircon make it warm-mani-low
| FID4617 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | Localised to room | RMG > RH > 13 > Ward 1310-1318, RMG |  | 2021-12-18 22:37:52 | 2021-12-18 22:39:49 | 2021-12-18 22:40:16 | 2021-12-18 22:42:20 | 2021-12-18 22:44:01 | 2021-12-18 22:45:37 | room setpoint adjust 24 to 26 aircon make it warm | [6 empty] | Aircon make it warm -aru-low
| FID4616 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > A&E |  | 2021-12-18 21:59:05 | 2021-12-18 21:59:31 | 2021-12-18 22:00:04 | 2021-12-18 22:00:35 | 2021-12-18 22:04:55 | 2021-12-18 22:07:18 | Replaced new bulb | [6 empty] | Light fused-mani-low
| FID4615 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1009 |  | 2021-12-18 21:19:28 | 2021-12-20 10:35:05 | 2021-12-20 10:35:29 | 2021-12-20 10:35:54 | 2021-12-20 10:36:19 | 2021-12-20 10:37:30 | Reduce the room vav damper position in bms system to make it warm | [6 empty] | Aircon make it warm -aru-low
| FID4612 | Office and Furniture | Safe Box | Cannot open / close | More than 1 room | RMG > RH > 13 > Ward 1328-1336 Nurse Station |  | 2021-12-18 20:20:30 | 2021-12-18 20:32:21 | 2021-12-18 20:32:49 | 2021-12-18 20:33:16 | 2021-12-18 20:35:17 | 2021-12-18 20:36:40 | cabinet number locker cannot open master key use open | [6 empty] | Patient locker cannot lock-v.bala-low
| FID4611 | Plumbing & Sanitary | Basin / sink | Choked | More than 1 room | RMG > RH > 12 > Housekeeping Office |  | 2021-12-18 20:01:11 | 2021-12-18 20:37:23 | 2021-12-18 20:37:48 | 2021-12-18 20:38:11 | 2021-12-18 20:38:49 | 2021-12-18 20:39:26 | choke clear | [6 empty] | Basin choke-v.bala-low
| FID4608 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1328-1336 |  | 2021-12-18 18:24:19 | 2021-12-18 18:25:01 | 2021-12-18 18:25:33 | 2021-12-18 18:26:03 | 2021-12-18 18:29:38 | 2021-12-18 19:04:29 | adjusted vav control in bms make it warm | [6 empty] | Aircon too cold, make it warm-v.bala-low
| FID4606 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1351-1357 |  | 2021-12-18 17:12:16 | 2021-12-18 17:31:45 | 2021-12-18 17:32:12 | 2021-12-18 17:34:52 | 2021-12-18 17:37:06 | 2021-12-18 17:38:09 | adjusted vav control in bms make it cool | [6 empty] | Aircon too cold, make it warm-v.bala-low
| FID4603 | Office and Furniture | TV | Cannot operate / defective | More than 1 room | RMG > RH > 10 > Ward 1007 |  | 2021-12-18 14:27:49 | 2021-12-18 14:48:17 | 2021-12-18 14:48:41 | 2021-12-18 14:49:11 | 2021-12-18 14:49:33 | 2021-12-18 14:50:27 | Power failure reset back to normal | [6 empty] | TV not working-Senthil-low
| FID4601 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1337-1343 |  | 2021-12-18 13:59:45 | 2021-12-18 14:00:15 | 2021-12-18 14:00:40 | 2021-12-18 14:00:51 | 2021-12-18 14:02:24 | 2021-12-18 14:03:37 | adjusted the temprature aircon make it warm | [6 empty] | Aircon make it warm-a.bala-low
| FID4600 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Nursing Stn C |  | 2021-12-18 13:35:55 | 2021-12-18 14:45:49 | 2021-12-18 14:46:29 | 2021-12-18 14:50:26 | 2021-12-18 14:51:25 | 2021-12-18 14:52:15 | air | [6 empty] | Aircon stuffy-nazri-low
| FID4598 | Mechanical | AHU / FCU / CU | Other: Room pressure low | Localised to room | RMG > RH > 9 > Ward 954 (BMT) |  | 2021-12-18 12:02:12 | 2021-12-20 10:31:49 | 2021-12-20 10:32:14 | 2021-12-20 10:32:38 | 2021-12-20 10:33:02 | 2021-12-20 10:33:47 | Adjusted the temperature setpoint on the isolation room display panel from 21c to 19c | [6 empty] | Room pressure low-nazri-low
| FID4597 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-18 12:00:42 | 2021-12-18 12:33:40 | 2021-12-18 12:34:01 | 2021-12-18 12:34:29 | 2021-12-18 12:34:50 | 2021-12-18 12:38:31 | Adjusted the aircon temperature make it warm | [6 empty] | Aircon make it cool-satha-low
| FID4595 | Mechanical | AHU / FCU / CU | Unserviceable | Localised to room | RMG > RH > 7 > Angio Suite |  | 2021-12-18 11:51:03 | 2021-12-20 10:28:08 | 2021-12-20 10:28:48 | 2021-12-20 10:29:16 | 2021-12-20 10:29:40 | 2021-12-20 10:30:18 | Replaced new AAA battery for hygrometer | [6 empty] | Hygrometer no battery-Allan-low
| FID4594 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1011 |  | 2021-12-18 11:49:11 | 2021-12-18 12:41:12 | 2021-12-18 12:42:52 | 2021-12-18 12:45:44 | 2021-12-18 12:56:57 | 2021-12-18 12:57:34 | Adjusted the room vav temperature setpoint and damper position in bms system | [6 empty] | Aircon make it warm-ilayaraja-low
| FID4593 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 13 > Ward 1345-1350 |  | 2021-12-18 11:48:22 | 2021-12-18 15:16:41 | 2021-12-18 15:17:07 | 2021-12-18 15:17:40 | 2021-12-18 15:18:06 | 2021-12-18 15:18:53 | Change Battery | [6 empty] | Wall clock not working-Allan-low
| FID4592 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 13 > Ward 1351-1357 |  | 2021-12-18 11:47:15 | 2021-12-18 12:23:05 | 2021-12-18 12:30:40 | 2021-12-18 12:31:04 | 2021-12-18 12:31:38 | 2021-12-18 12:32:42 | Adjusted the room vav temperature setpoint in bms system make it warm | [6 empty] | Aircon make it warm-satha-low
| FID4591 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1345-1350 |  | 2021-12-18 11:45:15 | 2021-12-18 12:07:21 | 2021-12-18 12:13:42 | 2021-12-18 12:19:12 | 2021-12-18 12:21:07 | 2021-12-18 12:22:16 | Adjusted the aircon temperature for the room vav in bms system make it warm | [6 empty] | Aircon make it warm-satha-low
| FID4590 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 8 > Ward 851 |  | 2021-12-18 11:27:46 | 2021-12-18 11:38:46 | 2021-12-18 11:39:38 | 2021-12-18 11:41:26 | 2021-12-18 11:42:43 | 2021-12-18 11:44:10 | replaced new light bulb | [6 empty] | Mirror light fused-nazri-low
| FID4589 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > RM@RH Counter |  | 2021-12-18 11:23:53 | 2021-12-18 11:36:19 | 2021-12-18 11:37:22 | 2021-12-18 11:49:41 | 2021-12-18 11:50:14 | 2021-12-18 11:51:39 | replaced new light bulb | [6 empty] | Light bulb fused -a.bala-low
| FID4587 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 852 |  | 2021-12-18 10:30:14 | 2021-12-18 10:38:11 | 2021-12-18 11:07:19 | 2021-12-18 11:08:08 | 2021-12-18 11:08:38 | 2021-12-18 11:09:41 | adjusted the cool8ng valve | [6 empty] | Aircon too warm-nazri-low
| FID4582 | Mechanical | Air Diffuser (supply/return) | Airflow too strong / weak | Localised to room | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-18 07:30:17 | 2021-12-18 07:31:16 | 2021-12-18 07:33:16 | 2021-12-18 07:34:15 | 2021-12-18 07:42:00 | 2021-12-18 07:43:29 | close the valve to 50 % from 100 % | [6 empty] | satha , low
| FID4581 | Medical Equipment | Autoclave | Leaking | Localised to room | RMG > RH > 7 > CSSD |  | 2021-12-18 07:17:02 | 2021-12-18 07:18:56 | 2021-12-18 07:19:47 | 2021-12-18 07:38:10 | 2021-12-18 07:40:53 | 2021-12-18 07:44:45 | cssd Autoclave 3 water leaking from hose need to arrange the contrectar for replace the hose | [6 empty] | ilayaraja, medium
| FID4580 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | More than 1 room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-18 03:12:13 | 2021-12-18 03:14:07 | 2021-12-18 03:14:34 | 2021-12-18 03:15:01 | 2021-12-18 03:19:56 | 2021-12-18 03:21:41 | checked setting on BMS motor running in 45 Hz reduce to 30 Hz and setpoint increased from 16 degree to 19 degree . checked on site back to normal | [6 empty] | satha , low
| FID4578 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1319-1327 |  | 2021-12-17 22:44:10 | 2021-12-17 22:45:54 | 2021-12-17 22:46:25 | 2021-12-17 22:46:51 | 2021-12-17 22:55:36 | 2021-12-17 22:57:47 | change to manual mode running normally . DDC no signal to run . need to inform Honeywell. | [6 empty] | satha , low
| FID4572 | Office and Furniture | Table | Misaligned / dangling | Localised to room | RMG > RH > 7 > Operating Theatre 10 |  | 2021-12-17 17:52:10 | 2021-12-18 10:48:14 | 2021-12-18 10:48:34 | 2021-12-18 10:48:56 | 2021-12-18 10:49:58 | 2021-12-18 10:51:30 | Fixed back the wheel | [6 empty] | Hand table wheel come out-nazri-low
| FID4570 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 12 |  | 2021-12-17 17:33:08 | 2021-12-18 09:43:13 | 2021-12-18 09:43:35 | 2021-12-18 09:43:58 | 2021-12-18 09:45:50 | 2021-12-18 09:46:36 | Adjusted the aircon temperature from 23c to 18c and damper from auto to 0% manual in bms system make it cool | [6 empty] | Aircon make it cool-Su-low
| FID4569 | Plumbing & Sanitary | Basin / sink | No water | Affecting Public | RMG > RH > 7 > OR9&10 Scrub Rm |  | 2021-12-17 17:31:01 | 2021-12-18 10:43:55 | 2021-12-18 10:44:17 | 2021-12-18 10:44:41 | 2021-12-18 10:45:03 | 2021-12-18 10:47:23 | Checked on site, water coming out but, low pressure. Adjusted the valve, basin water back to normal | [6 empty] | Scrub sink no water-nazri-low
| FID4568 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Localised to room | RMG > RH > 9 > Ward 917 |  | 2021-12-17 17:29:55 | 2021-12-18 10:21:47 | 2021-12-18 10:24:21 | 2021-12-18 10:24:52 | 2021-12-18 10:25:18 | 2021-12-18 10:25:58 | replaced new bidet spray | [6 empty] | Bidet spray leaking -nazri-low
| FID4566 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 12 |  | 2021-12-17 16:06:04 | 2021-12-17 16:06:28 | 2021-12-17 16:06:47 | 2021-12-17 16:07:07 | 2021-12-17 16:07:55 | 2021-12-17 16:09:48 | Adjusted the temperature setpoint from 23c to 18c in bms system make it cool. Heater automatically reduced from 65% to 14%. | [6 empty] | Aircon make it cool-su-low
| FID4565 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > Concierge |  | 2021-12-17 15:31:26 | 2021-12-17 15:42:02 | 2021-12-17 15:42:32 | 2021-12-17 15:42:56 | 2021-12-17 15:44:28 | 2021-12-17 15:48:24 | Replaced new bulb 2 nos | [6 empty] | Light fused -mani-low
| FID4564 | Electrical | Light Bulb | Misaligned / dangling | Localised to room | RMG > RH > 2 > Raffles Chinese Medicine Clinic |  | 2021-12-17 14:59:12 | 2021-12-17 15:00:46 | 2021-12-17 15:01:13 | 2021-12-17 15:01:55 | 2021-12-17 15:02:27 | 2021-12-17 15:06:56 | Replaced new screw | [6 empty] | Light fitting screw loose-mani-low
| FID4563 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 13 |  | 2021-12-17 14:24:54 | 2021-12-17 14:34:26 | 2021-12-17 14:34:50 | 2021-12-17 14:35:11 | 2021-12-17 14:35:31 | 2021-12-17 14:40:04 | Check on site ,Ahu 13-1 was on manual.,put back to auto mode..actuator upon checking not responding,.highlight to honeywell to follow up | [6 empty] | Aircon too cold whole ward, make it warm-Isyamudin-low
| FID4562 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-17 14:20:17 | 2021-12-17 15:28:24 | 2021-12-17 15:28:45 | 2021-12-17 15:36:01 | 2021-12-17 15:37:06 | 2021-12-17 15:38:08 | vav tamber manually open | [6 empty] | Aircon make it cool -Aru-low
| FID4561 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1048 |  | 2021-12-17 14:18:52 | 2021-12-17 14:20:55 | 2021-12-17 14:21:23 | 2021-12-17 14:21:43 | 2021-12-17 14:22:00 | 2021-12-17 14:23:07 | Adjusted the vav 1-1-28 temperature setpoint from 24c to 22c and damper position from 5% manual to auto (56.3%) in bms system make it cool. | [6 empty] | Aircon make it cool -Su-low
| FID4559 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 2 > Skin & Aesthetics Consult Rm 6 |  | 2021-12-17 14:04:30 | 2021-12-17 14:05:10 | 2021-12-17 14:05:28 | 2021-12-17 14:06:43 | 2021-12-17 14:07:01 | 2021-12-17 14:09:07 | Adjusted vav 5-1-7 temperature setpoint from 22c to 24c and damper position from 50% manual to 30% in bms system make it warm. | [6 empty] | Aircon too cold, make it warm-Su-low
| FID4558 | Plumbing & Sanitary | Urinal | Choked | Localised to room | RMG > RSC > 2 > Male Toilet |  | 2021-12-17 14:03:12 | 2021-12-18 11:07:19 | 2021-12-18 11:07:39 | 2021-12-18 11:07:59 | 2021-12-18 11:08:30 | 2021-12-18 11:08:59 | Cleared the urinal choke | [6 empty] | Urinal bowl choke-v.bala-low
| FID4557 | Building | Window | Unable to open or close properly | Localised to room | RMG > RH > 12 > RHS Female Toilet |  | 2021-12-17 14:01:21 | 2021-12-17 14:58:58 | 2021-12-17 15:41:09 | 2021-12-17 17:22:47 | 2021-12-17 17:23:10 | 2021-12-17 17:24:56 | Put down the curtains | [6 empty] | Window blind faulty - ming cai-low
| FID4553 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU Rm 708 |  | 2021-12-17 12:39:20 | 2021-12-17 13:07:09 | 2021-12-17 13:07:35 | 2021-12-17 13:08:44 | 2021-12-17 13:58:05 | 2021-12-17 13:58:43 | Manually close the room vav damper | [6 empty] | aircon to cold ,make it warm -aru-low
| FID4552 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RSC > 8 > ENT |  | 2021-12-17 11:40:01 | 2021-12-18 11:14:39 | 2021-12-18 11:15:01 | 2021-12-18 11:15:23 | 2021-12-18 11:16:13 | 2021-12-18 11:17:30 | Need to purchase bulb. Will follow-up | [6 empty] | Light fused-mani-low
| FID4551 | Mechanical | Auto Sliding Glass Door | Cannot Open or Close | Localised to room | RMG > RSC > 13 > Link Bridge |  | 2021-12-17 11:05:06 | 2021-12-18 11:18:48 | 2021-12-18 11:19:10 | 2021-12-18 11:19:32 | 2021-12-18 11:19:54 | 2021-12-18 11:21:28 | Unable to rectify the door issue. Engaged entre contractor to check. Work done | [6 empty] | Door slam very loud and EM lock not touching-a.bala-low
| FID4550 | Mechanical | Auto Sliding Glass Door | Other: EM lock not touching | Localised to room | RMG > RSC > 19 > Level 19 |  | 2021-12-17 11:03:39 | 2021-12-18 10:57:56 | 2021-12-18 10:58:17 | 2021-12-18 10:58:37 | 2021-12-18 10:59:02 | 2021-12-18 11:03:38 | Adjusted the EM door alignment, EM lock working back to normal. | [6 empty] | Need to check alignment of the EM door, EM lock not touching-v.bala-low
| FID4549 | Office and Furniture | Cabinet | Cannot open / close | Localised to room | RMG > RH > 11 > Room 1107 (QM) |  | 2021-12-17 11:00:31 | 2021-12-17 11:02:04 | 2021-12-17 11:38:49 | 2021-12-17 11:39:20 | 2021-12-17 11:40:02 | 2021-12-17 13:08:25 | Change a new cabinet | [6 empty] | Top-hanging cabinet cannot lock-ming cai-low
| FID4546 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-17 10:34:26 | 2021-12-18 09:49:33 | 2021-12-18 09:49:54 | 2021-12-18 09:50:16 | 2021-12-18 09:50:41 | 2021-12-18 10:09:10 | Replaced new cylinders | [6 empty] | Need to replace 2 big CO2 cylinder-nazri-medium
| FID4545 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-17 10:32:28 | 2021-12-17 10:44:13 | 2021-12-17 10:44:33 | 2021-12-17 10:44:59 | 2021-12-17 10:45:23 | 2021-12-17 10:48:48 | Adjusted the temperature setpoint from 25c to 18c and heater from 100% manual to auto (0%) in bms system make it cool. | [6 empty] | Aircon make it cool -Su-low
| FID4544 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1358-1363 |  | 2021-12-17 10:30:46 | 2021-12-17 10:35:54 | 2021-12-17 10:38:17 | 2021-12-17 10:38:37 | 2021-12-17 10:38:55 | 2021-12-17 10:43:44 | Adjusted the vav number 1-2-15 damper position from 20% to 5% and vav 1-2-16 temperature setpoint from 24c to 26c and damper from 20% to 5% in bms system make it warm | [6 empty] | Aircon make it warm -su-low
| FID4543 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 12 > REMC Counter |  | 2021-12-17 10:29:09 | 2021-12-17 11:05:17 | 2021-12-17 11:09:48 | 2021-12-17 11:10:32 | 2021-12-17 11:10:58 | 2021-12-17 11:12:57 | aircon make it cool colling valve adjust 40 to 60 | [6 empty] | Aircon make it cool -Aru-low
| FID4542 | Building | Door Lock | Unable to open or close properly | Localised to room | RMG > RSC > 11 > Radiology |  | 2021-12-17 10:23:48 | 2021-12-17 12:49:36 | 2021-12-17 12:49:53 | 2021-12-17 13:02:55 | 2021-12-17 13:03:15 | 2021-12-17 15:05:49 | open the lock | [6 empty] | Door lock faulty -ming cai-low
| FID4539 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 7 > ICU Rm 705 |  | 2021-12-17 10:17:24 | 2021-12-17 10:37:38 | 2021-12-17 10:39:37 | 2021-12-17 10:40:35 | 2021-12-17 10:41:32 | 2021-12-17 10:44:26 | call bell rreset back to normal | [6 empty] | Call bell not ringing-a.bala-low
| FID4537 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 16 > Eye Centre Consult Rm 1 |  | 2021-12-17 10:15:50 | 2021-12-17 11:06:59 | 2021-12-17 11:07:25 | 2021-12-17 11:08:43 | 2021-12-17 11:09:06 | 2021-12-17 11:12:29 | Adjusted VAV 16-2-4 temperature setpoint to 24c and damper position to 20% manual in bms system | [6 empty] | Aircon make it warm-ilayaraja-low
| FID4536 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > RHS Male Toilet |  | 2021-12-17 10:09:51 | 2021-12-17 10:49:39 | 2021-12-17 10:51:35 | 2021-12-17 10:52:47 | 2021-12-17 10:53:39 | 2021-12-17 10:54:31 | replaced new light bulb | [6 empty] | Ceiling light fused-a.bala-low
| FID4535 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2021-12-17 10:06:57 | 2021-12-17 10:12:23 | 2021-12-17 11:52:21 | 2021-12-17 11:53:18 | 2021-12-17 11:56:28 | 2021-12-17 14:12:39 | Cabinet drawer number lock cannot open. Used master key to open the cabinet drawer | [6 empty] | Need to open patient safe drawer-v.bala-low
| FID4533 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 7 |  | 2021-12-17 09:47:03 | 2021-12-17 10:12:04 | 2021-12-17 10:12:33 | 2021-12-17 10:13:01 | 2021-12-17 10:13:28 | 2021-12-17 10:24:13 | then just put 'Suspect dimmer switch problem. When dim light, light flickering. | [6 empty] | Light flickering -mani-low
| FID4529 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-17 07:22:13 | 2021-12-17 07:26:17 | 2021-12-17 07:26:47 | 2021-12-17 07:39:55 | 2021-12-17 07:40:23 | 2021-12-17 07:42:04 | adjusted setpoint fot OT 8 from 18 to 25 degree and active heater | [6 empty] | Aircon make it warm to 24c for paeds case-ilayaraja-low
| FID4528 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-17 07:18:42 | 2021-12-17 07:19:32 | 2021-12-17 07:22:51 | 2021-12-17 07:23:26 | 2021-12-17 07:25:19 | 2021-12-17 07:27:40 | checked on BMS setpoint on 15 degree so increase setpoint to 16 degree | [6 empty] | Aircon make warm, very cool in all place -satha-low
| FID4527 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1319-1327 Nurse Station |  | 2021-12-17 01:35:07 | 2021-12-17 01:36:41 | 2021-12-17 01:37:28 | 2021-12-17 01:38:08 | 2021-12-17 01:39:18 | 2021-12-17 01:41:27 | setpoint temperature is in auto 24 degrees and vav opening position only 20 % . but still patient need to warm so adjusted VAV position to 10 %. | [6 empty] | Aircon make it warm -satha-low
| FID4523 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1011 |  | 2021-12-16 18:47:27 | 2021-12-16 18:48:01 | 2021-12-16 18:48:42 | 2021-12-16 18:49:11 | 2021-12-16 18:49:37 | 2021-12-16 18:55:19 | adjusted the temperature setpoint form 24c to 30c and heater form auto to 100% manual in bms system | [6 empty] | Aircon make it warm -mani-low
| FID4518 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 852 |  | 2021-12-16 16:09:08 | 2021-12-16 16:28:39 | 2021-12-16 17:08:02 | 2021-12-16 17:08:23 | 2021-12-16 17:08:44 | 2021-12-16 17:10:50 | Check on-site ahu 8-1 actuator jam..highlighted honeywell to follow up. | [6 empty] | Aircon make it cool-isyamudin-low
| FID4513 | Plumbing & Sanitary | Soap Dispenser | Other: FIx new | Localised to room | RMG > RH > 8 > Labour Ward Counter |  | 2021-12-16 14:58:35 | 2021-12-16 15:05:24 | 2021-12-16 15:06:24 | 2021-12-16 15:07:48 | 2021-12-16 15:09:06 | 2021-12-16 15:10:03 | work completed | [6 empty] | Need to remove old hand rub dispenser and install new one -v.bala-low
| FID4512 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 10 > Heart Ctr Con Rm 5 |  | 2021-12-16 14:57:11 | 2021-12-16 15:02:03 | 2021-12-16 15:02:23 | 2021-12-16 15:02:43 | 2021-12-16 15:03:07 | 2021-12-16 15:03:54 | Adjusted VAV 10-1-17 temperature setpoint at 18c and damper from 85% manual to 95% manual in bms system make it cool slightly. | [6 empty] | Aircon make it slightly cool-su-low
| FID4511 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 10 |  | 2021-12-16 14:56:18 | 2021-12-16 14:59:16 | 2021-12-16 14:59:53 | 2021-12-16 15:00:27 | 2021-12-16 15:00:51 | 2021-12-16 15:01:31 | Adjusted the temperature setpoint from 23c to 26c and heater from auto to 100% manual in bms system | [6 empty] | Aircon make it warm-su-low
| FID4506 | Plumbing & Sanitary | Tap | Leaking | Localised to room | RMG > RH > 7 > Clinical Lab |  | 2021-12-16 13:36:31 | 2021-12-16 13:47:26 | 2021-12-16 13:47:50 | 2021-12-16 13:48:14 | 2021-12-16 14:38:29 | 2021-12-16 17:45:29 | Need to purchase new tap. Awaiting for parts. | [6 empty] | Basin tap leaking-v.bala-low
| FID4505 | Electrical | Call System | Other: Keep ringing | Affecting Public | RMG > RH > 7 > OT |  | 2021-12-16 13:35:17 | 2021-12-16 13:36:00 | 2021-12-16 13:48:23 | 2021-12-16 13:48:44 | 2021-12-16 13:49:08 | 2021-12-16 15:11:42 | replaced spare faceplate | [6 empty] | Call bell keep ringing non-stop-mani-low
| FID4504 | Plumbing & Sanitary | Basin / sink | Leaking | Affecting Public | RMG > RH > 9 > Nursing Stn D |  | 2021-12-16 13:33:40 | 2021-12-16 13:35:18 | 2021-12-16 13:38:05 | 2021-12-16 14:40:41 | 2021-12-16 14:41:46 | 2021-12-16 15:14:01 | onside checked no leaking | [6 empty] | Water leaking from basin-v.bala-low
| FID4503 | Electrical | Call System | Other: Keep ringing | Localised to room | RMG > RH > 7 > Day Surgery |  | 2021-12-16 13:31:33 | 2021-12-16 13:36:05 | 2021-12-16 13:50:12 | 2021-12-16 13:51:10 | 2021-12-16 13:51:59 | 2021-12-16 14:02:18 | reset back to normal | [6 empty] | Call bell keep ringing non stop-a.bala-low
| FID4502 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 11 > Admin Office Corridor |  | 2021-12-16 13:16:01 | 2021-12-16 16:06:21 | 2021-12-16 16:06:43 | 2021-12-16 16:07:05 | 2021-12-16 16:07:46 | 2021-12-16 16:08:22 | checked on site after adjust bms. ok | [6 empty] | Aircon too cold-aru-low
| FID4500 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 7 > Molecular Lab PCR Rm |  | 2021-12-16 12:07:48 | 2021-12-16 12:10:42 | 2021-12-16 12:11:13 | 2021-12-16 12:11:38 | 2021-12-16 12:12:14 | 2021-12-16 12:17:02 | Replaced new bulb 5 nos | [6 empty] | Need to replace fused bulb-mani-low
| FID4499 | Building | Wall | Other: Photo frame | Localised to room | RMG > RH > 8 > Labour Ward Nursery |  | 2021-12-16 11:03:38 | 2021-12-16 15:18:08 | 2021-12-16 15:19:50 | 2021-12-16 15:23:47 | 2021-12-16 16:22:02 | 2021-12-16 16:22:26 | [7 empty] | Photo frame dropped-isyamudin-low
| FID4496 | Plumbing & Sanitary | WC / Squatting Pedestal | Water flowing non-stop | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2021-12-16 10:44:16 | 2021-12-16 13:43:48 | 2021-12-16 13:44:11 | 2021-12-16 13:44:47 | 2021-12-16 13:45:10 | 2021-12-16 13:45:47 | flushing head screw adjusted and settled | [6 empty] | Toilet flush not working-v.bala-low
| FID4494 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-16 10:42:57 | 2021-12-16 11:16:59 | 2021-12-16 11:17:49 | 2021-12-16 11:18:12 | 2021-12-16 11:18:37 | 2021-12-16 11:21:06 | Check station D temperature ok.cant find anyone give the feedback | [6 empty] | Aircon make it warm-a.bala.low
| FID4493 | Plumbing & Sanitary | WC / Squatting Pedestal | Water flowing non-stop | Localised to room | RMG > RH > 13 > Ward 1358-1363 Nurse Station |  | 2021-12-16 10:40:39 | 2021-12-16 13:40:12 | 2021-12-16 13:40:36 | 2021-12-16 13:40:58 | 2021-12-16 13:41:38 | 2021-12-16 13:42:34 | settled non stop flushing complaint | [6 empty] | Toilet flushing non-stop-aru-low
| FID4492 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > Skin & Aesthetics Consult Rm 6 |  | 2021-12-16 10:36:53 | 2021-12-16 11:07:24 | 2021-12-16 11:07:49 | 2021-12-16 11:25:30 | 2021-12-16 11:25:53 | 2021-12-16 11:26:47 | Adjusted vav 5-1-7 temperature setpoint from 20c to 22c and damper from auto to 50% manual in bms system make it warm | [6 empty] | Aircon too cold, make it warm-Su-low
| FID4488 | Building Security System | CCTV System | Disconnected | Localised to room | RMG > RH > 11 > Bed Lift Lobby |  | 2021-12-16 10:28:26 | 2021-12-16 10:31:15 | 2021-12-16 10:45:18 | 2021-12-16 10:45:45 | 2021-12-16 10:46:10 | 2021-12-16 11:00:18 | Power Reset normal back | [6 empty] | cctv camera not working mani -low
| FID4486 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 1 (Endoscopy) |  | 2021-12-16 09:55:59 | 2021-12-16 10:04:53 | 2021-12-16 10:05:42 | 2021-12-16 10:06:43 | 2021-12-16 10:07:40 | 2021-12-16 10:08:28 | Adjusted the temperature setpoint and heater to 0% manual in bms system | [6 empty] | Aircon make it cool, now showing 24c-Su-low
| FID4485 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-16 09:54:53 | 2021-12-16 10:00:25 | 2021-12-16 10:00:52 | 2021-12-16 10:01:17 | 2021-12-16 10:02:19 | 2021-12-16 10:03:04 | Adjusted the temperature setpoint from 22c to 18c and heater from 100% manual to 0% manual in bms system | [6 empty] | Aircon make it cool to 18c, now showing 21c-Su-low
| FID4484 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > Nuclear Medicine Centre |  | 2021-12-16 09:52:11 | 2021-12-16 10:05:06 | 2021-12-16 10:10:31 | 2021-12-16 10:10:55 | 2021-12-16 10:11:34 | 2021-12-16 10:12:10 | replace new bulb |  |  |  |  | 1 |  | Toilet light fused-a.bala-low
| FID4483 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 2 |  | 2021-12-16 09:50:21 | 2021-12-16 09:56:55 | 2021-12-16 09:57:20 | 2021-12-16 09:57:43 | 2021-12-16 09:58:08 | 2021-12-16 09:59:09 | Adjusted VAV 5-1-5 temperature setpoint from 22c to 20c and damper position from 21.2% (auto) to 70% manual in bms system | [6 empty] | No aircon -Su-low
| FID4482 | Medical Equipment | Medical Gas | Other: medical gas O2 terminal leaking | Localised to room | RMG > RH > 8 > Ward 850 |  | 2021-12-16 09:31:26 | 2021-12-16 09:31:59 | 2021-12-16 09:32:20 | 2021-12-16 09:32:38 | 2021-12-16 09:32:42 | 2021-12-16 11:09:11 | ACA contractor replaced new oxygen terminal and o-rings |  | 2021-12-16 09:33:37 |  |  |  |  | medical gas O2 terminal leaking-Shanmu-medium
| FID4477 | Mechanical | BMS / BAS | Noisy | More than 1 room | RMG > RH > 10 > Ward 1060 |  | 2021-12-16 00:36:22 | 2021-12-16 00:40:18 | 2021-12-16 10:24:03 | 2021-12-16 10:24:26 | 2021-12-16 10:24:49 | 2021-12-16 10:26:06 | Adjusted room vav temperature setpoint in bms system make it cool | [6 empty] | Room aircon stuffy-v.bala-low