## Sheet1
Fault 2022-01-04 14:35:01
Fault Number | Building Trade | Trade Category | Type of Fault | Impact | Location | Cancel Status | Reported Date | Fault Acknowledged Date | Responded on Site Date | RA Conducted Date | Work Started Date | Work Completed Date | Action(s) Taken | Other Trades Required Date | Cost Cap Exceed Date | Assistance Requested Date | Fault Reference | End User Name | End User Priority | End User Contact | Incident Report | Reported By | Remarks
FID5279 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 8 > Delivery Suite 7 |  | 2021-12-31 19:48:29 | [14 empty] | FRC | Bed head light fused-abala-low
FID5278 | Mechanical | AHU / FCU / CU | System Shows fault / Error code | Affecting Public | RMG > RH > 7 > Operating Theatre 10 |  | 2021-12-31 16:45:44 | [14 empty] | FRC | Humidity indicates 90% and temperature 60c on the display panel. Need to check. -Isyamudin-low
FID5275 | Building | Water Dispenser | Other: Tap button come out | Affecting Public | RMG > RH > 8 > Stn C Pantry |  | 2021-12-31 15:27:39 | 2021-12-31 18:10:09 | 2021-12-31 18:10:32 | 2021-12-31 18:10:54 | 2021-12-31 18:11:18 | 2021-12-31 18:12:05 | Have checked with the user now we don’t have stock |  |  |  |  | Helen (8B) |  |  |  | FRC | Water dispenser hot water tap button come out-Allan-low
FID5274 | Building | Window Panel | Other: Curtain stuck | Affecting Public | RMG > RH > 13 > Ward 1351-1357 |  | 2021-12-31 15:02:39 | 2021-12-31 15:03:27 | 2021-12-31 15:26:11 | 2021-12-31 15:26:39 | [11 empty] | FRC | Curtain stuck-Hossain-low
FID5271 | Mechanical | AHU / FCU / CU | System Shows fault / Error code | Affecting Public | RMG > RH > 6 > UPS Rm |  | 2021-12-31 14:02:04 | [10 empty] | Li Fei |  |  |  | FRC | Aircon not working-Satha-low
FID5270 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 8 > Delivery Suite 7 |  | 2021-12-31 13:55:38 | [14 empty] | FRC | Toilet mirror light fused-a.bala-low
FID5269 | Building | Floor | Other: Carpet come out | Affecting Public | RMG > RSC > 12 > Visitor Lift Lobby |  | 2021-12-31 13:54:03 | 2021-12-31 15:05:15 | 2021-12-31 15:05:45 | 2021-12-31 15:06:05 | 2021-12-31 15:06:27 | 2021-12-31 15:07:29 | Stick back | [8 empty] | FRC | Carpet come out-ming cai-low
FID5266 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 13 > Ward 1328-1336 Nurse Station |  | 2021-12-31 13:40:23 | 2021-12-31 13:45:12 | 2021-12-31 13:45:55 | 2021-12-31 13:46:32 | 2021-12-31 13:47:04 | 2021-12-31 14:00:44 | Adjusted VAV 1-2-9 damper position from 30% auto to 60% manual in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5265 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 13 > Ward 1328-1336 |  | 2021-12-31 13:39:34 | 2021-12-31 13:42:21 | 2021-12-31 13:43:01 | 2021-12-31 13:43:30 | 2021-12-31 13:43:53 | 2021-12-31 13:59:22 | Adjusted vav 1-1-8 temperature setpoint from 25c to 22c and damper from 5% manual to auto (68.8%) in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5262 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 9 > Nursing Stn B |  | 2021-12-31 12:51:03 | [10 empty] | staff | 1 |  |  | FRC | Aircon too cold, make it warm-Satha-low
FID5257 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > Passenger Lift Lobby |  | 2021-12-31 11:47:51 | [10 empty] | Jia Jing |  |  |  | FRC | Light flickering -A.Bala-low
FID5255 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 12 > Women Centre Consult Rm 19 |  | 2021-12-31 10:47:38 | 2021-12-31 12:09:47 | 2021-12-31 12:11:06 | 2021-12-31 12:12:25 | 2021-12-31 12:13:30 | 2021-12-31 12:14:57 | replaced new light bulb | [8 empty] | FRC | Light bulb fused -a.bala-low
FID5254 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Affecting Public | RMG > RH > 13 > Male Toilet (Waiting Area) |  | 2021-12-31 10:46:16 | 2021-12-31 13:02:30 | 2021-12-31 13:02:54 | 2021-12-31 13:03:13 | 2021-12-31 13:03:32 | 2021-12-31 13:04:33 | Bidet I have change a new set | [8 empty] | FRC | Bidet spray broken-Allan-low
FID5249 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 11 > CT Scan Room 25 |  | 2021-12-31 10:25:36 | [14 empty] | FRC | Aircon make it cool-isyamudin-low
FID5248 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 11 > Fluoroscopy Control Rm |  | 2021-12-31 10:24:21 | [14 empty] | FRC | Aircon make it cool-isyamudin-low
FID5246 | Electrical | PA System | Other: Need to turn off music | Affecting Public | RMG > RSC > 8 > Counselling Ctr Rm 9 |  | 2021-12-31 10:22:09 | 2022-01-04 13:33:51 | [13 empty] | FRC | Need to turn off the music-Li fei-low
FID5245 | Medical Equipment | Commode Chair | Other: Trolley bed | Affecting Public | RMG > RH > 7 > Day Surgery |  | 2021-12-31 10:20:36 | 2022-01-04 13:35:44 | 2022-01-04 13:36:06 | 2022-01-04 13:36:29 | [11 empty] | FRC | Patient trolley bed wheel broken - Hossain-low
FID5237 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 8 > Stn D Corridor |  | 2021-12-31 08:21:13 | 2022-01-04 13:25:30 | 2022-01-04 13:25:55 | 2022-01-04 13:26:37 | 2022-01-04 13:27:52 | 2022-01-04 13:28:27 | Adjusted the display | [8 empty] | Rajendran Manikandan | display LED lights time not working -aru-low
FID5236 | Office and Furniture | TV | Cannot operate / defective | Localised to room | RMG > RH > 10 > Ward 1062 |  | 2021-12-31 08:13:28 | 2021-12-31 08:15:20 | 2021-12-31 08:17:31 | 2021-12-31 08:17:49 | 2021-12-31 08:17:55 | 2021-12-31 08:22:07 | Replaced new battery | [8 empty] | FRC | tv remote not working-mani-low
FID5226 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1055 |  | 2021-12-30 18:04:06 | 2021-12-30 18:05:48 | 2021-12-30 18:06:12 | 2021-12-30 18:06:36 | 2021-12-30 18:06:55 | 2021-12-30 18:07:41 | Adjusted VAV 1-1-20 temperature setpoint from 24c to 26c and damper from 5% manual to 0% manual in bms system make it warm | [8 empty] | FRC | Aircon make it warm-su-low
FID5225 | Office and Furniture | TV | Cannot operate / defective | Affecting Public | RMG > RH > 10 > Ward 1049 |  | 2021-12-30 17:44:59 | 2022-01-03 13:14:56 | 2022-01-03 13:29:53 | 2022-01-03 13:33:55 | 2022-01-04 10:22:34 | 2022-01-04 10:23:05 | Replaced new battery for tv remote | [8 empty] | FRC | TV cannot on-a.bala-low
FID5224 | Plumbing & Sanitary | Tap | Damaged / Loose / Cracked | Affecting Public | RMG > RH > 13 > Ward 13 |  | 2021-12-30 17:44:15 | 2021-12-30 20:03:13 | 2021-12-30 20:03:33 | 2021-12-30 20:03:53 | 2021-12-30 20:04:16 | 2021-12-30 20:04:47 | repair |  |  |  |  | Felix |  |  |  | FRC | Basin tap loose-ming cai-low
FID5223 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 7 > ICU Rm 709 |  | 2021-12-30 17:42:30 | 2021-12-31 12:03:46 | 2021-12-31 12:04:45 | 2021-12-31 12:05:09 | 2021-12-31 12:05:30 | 2021-12-31 12:06:06 | Cleared the choke | [8 empty] | FRC | Basin choke-v.bala-low
FID5219 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 9 |  | 2021-12-30 17:01:01 | 2021-12-30 17:02:45 | 2021-12-30 17:03:06 | 2021-12-30 17:03:27 | 2021-12-30 17:03:58 | 2021-12-30 17:10:05 | Adjusted the heater position from auto to 0% manual in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5218 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-30 17:00:19 | 2021-12-30 17:04:46 | 2021-12-30 17:06:03 | 2021-12-30 17:06:26 | 2021-12-30 17:06:48 | 2021-12-30 17:14:53 | Adjusted the temperature setpoint from 28c to 20c and heater from 100% manual to auto (0%) in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5217 | Electrical | PA System | Other: No music | Affecting Public | RMG > RSC > 9 > Internal Med |  | 2021-12-30 16:59:28 | 2022-01-03 12:04:19 | 2022-01-03 12:04:56 | 2022-01-03 12:05:18 | 2022-01-03 12:06:42 | 2022-01-03 12:08:45 | Adjusted the PA volume | [8 empty] | FRC | Waiting area, counter no music-senthil-low
FID5216 | Electrical | Light Bulb | Misaligned / dangling | Localised to room | RMG > RH > 10 > Doctor's Lounge |  | 2021-12-30 16:47:23 | 2021-12-31 12:01:29 | 2021-12-31 12:01:51 | 2021-12-31 12:02:14 | 2021-12-31 12:02:36 | 2021-12-31 12:03:03 | Fixed back the light properly |  |  |  |  | Jasmine HK |  |  |  | FRC | Light bulb dangling-a.bala-low
FID5214 | Medical Equipment | Trolley | Other: Trolley lock cannot open | Affecting Public | RMG > RH > 8 > Nursing Stn B |  | 2021-12-30 15:59:51 | 2022-01-03 11:27:46 | 2022-01-03 11:30:52 | 2022-01-03 11:31:30 | 2022-01-03 11:31:56 | 2022-01-03 11:57:45 | Repaired the trolley lock | [8 empty] | FRC | Medication trolley lock cannot open-ming cai-low
FID5213 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1059 |  | 2021-12-30 15:45:45 | 2021-12-30 15:46:17 | 2021-12-30 15:46:37 | 2021-12-30 15:47:02 | 2021-12-30 15:52:01 | 2021-12-30 17:16:05 | Adjusted the vav 1-1-17 temperature setpoint from 24c to 26c and damper position from 5% manual to 0% manual in bms system make it warm | [8 empty] | FRC | Aircon make it warm-su-low
FID5208 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 10 > Ward 1043 |  | 2021-12-30 14:47:04 | 2021-12-30 16:14:24 | 2021-12-30 16:15:33 | 2021-12-31 11:59:52 | 2021-12-31 12:00:15 | 2021-12-31 12:00:44 | Fixed back the call bell panel | [8 empty] | FRC | Call bell panel come out-a.bala-low
FID5206 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1052 |  | 2021-12-30 14:34:18 | 2021-12-30 15:52:42 | 2021-12-30 15:54:35 | 2021-12-30 15:55:27 | 2021-12-30 15:57:25 | 2021-12-30 15:58:32 | Adjusted VAV 1-1-23 temperature setpoint from 24c to 22c in bms system make it cool. Damper position automatically increase from 20% to 90% | [8 empty] | FRC | Aircon make it cool-su-low
FID5205 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn D |  | 2021-12-30 14:33:03 | 2021-12-30 17:16:49 | 2021-12-30 17:17:31 | 2021-12-30 17:18:16 | 2021-12-30 17:18:37 | 2021-12-30 17:19:27 | Adjusted VAV 1-1-13 temperature setpoint to 22c and damper from auto to 100% manual in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5204 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 7 > Call Centre |  | 2021-12-30 14:32:10 | 2021-12-31 11:52:27 | 2021-12-31 11:52:48 | 2021-12-31 11:53:10 | 2021-12-31 11:53:31 | 2021-12-31 11:54:00 | Cleared the choke | [8 empty] | FRC | Basin choke-nazri-low
FID5203 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Affecting Public | RMG > RSC > 12 > Handicap Toilet |  | 2021-12-30 14:31:21 | 2021-12-31 11:55:44 | 2021-12-31 11:56:07 | 2021-12-31 11:56:27 | 2021-12-31 11:56:48 | 2021-12-31 11:57:35 | Replaced new bidet spray |  |  |  |  | abu housekeeping |  |  |  | FRC | Bidet spray leaking-nazri-low
FID5202 | Medical Equipment | Medical Gas | Change Cylinders | Affecting Public | RMG > RH > 7 > OT |  | 2021-12-30 14:30:28 | 2021-12-30 15:58:20 | 2021-12-30 15:58:50 | 2021-12-30 15:59:25 | 2021-12-31 11:58:21 | 2021-12-31 11:58:55 | Replaced new CO2 cylinder | [8 empty] | FRC | Need to replace 1 big CO2 cylinder-Hossain-medium
FID5200 | Plumbing & Sanitary | WC / Squatting Pedestal | Water flowing non-stop | Affecting Public | RMG > RH > 8 > Ward 850 |  | 2021-12-30 14:24:49 | 2021-12-31 12:06:45 | 2022-01-03 11:25:22 | 2022-01-03 11:25:48 | 2022-01-03 11:26:12 | 2022-01-03 11:26:48 | Adjusted the flushing system |  |  |  |  | HK |  |  |  | FRC | Toilet flushing non stop-v.bala-low
FID5199 | Building | Door Closer | Unable to open or close properly | Affecting Public | RMG > RH > 2 > RCM Consult Rm 8 |  | 2021-12-30 14:24:00 | 2022-01-03 11:01:15 | 2022-01-03 11:02:18 | 2022-01-03 11:21:35 | 2022-01-03 11:22:00 | 2022-01-03 11:23:55 | Repaired the door | [8 empty] | FRC | Door cannot close properly-V.Bala-low
FID5198 | Building | Door Frame | Unable to open or close properly | Affecting Public | RMG > RH > 1 > A&E Bed 10 |  | 2021-12-30 14:22:55 | 2021-12-31 11:46:47 | 2021-12-31 11:49:01 | 2021-12-31 11:49:23 | 2021-12-31 11:49:43 | 2021-12-31 11:50:16 | Fixed back the door frame |  |  |  |  | Adeline |  |  |  | FRC | Door frame come out-Ming cai-low
FID5195 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 9 |  | 2021-12-30 14:20:48 | 2021-12-31 11:37:12 | 2021-12-31 11:43:03 | 2021-12-31 11:44:09 | 2021-12-31 11:44:33 | 2021-12-31 11:46:05 | Checked AHU 13-3 not running in auto mode. Manually on AHU 13-3 and bypass the actuator to 100% fully open make cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5194 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-30 14:19:16 | 2021-12-31 11:28:59 | 2021-12-31 11:29:21 | 2021-12-31 11:31:02 | 2021-12-31 11:31:49 | 2021-12-31 11:35:29 | Checked and found AHU 13-3 not running in auto mode. Manually run the AHU onsite and bypass the actuator to 100% fully open to make cool. | [8 empty] | FRC | Aircon make it cool-Isyamudin-low
FID5193 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-30 14:18:25 | 2021-12-31 11:23:59 | 2021-12-31 11:24:21 | 2021-12-31 11:24:43 | 2021-12-31 11:26:42 | 2021-12-31 11:27:44 | Checked and found AHU 13-3 not running in auto mode. Manually turn on AHU 13-3 and bypass the actuator to 100% fully open to make cool. | [8 empty] | FRC | Aircon make it cool-isyamudin-low
FID5182 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 3 (Embryo Lab) |  | 2021-12-30 11:05:07 | 2021-12-30 11:06:14 | 2021-12-30 11:06:38 | 2021-12-30 11:07:01 | 2021-12-30 11:07:25 | 2021-12-31 11:08:50 | Adjusted the temperature setpoint from 18c to 24c and heater from 0% manual to 70% manual in bms system make it warm |  |  |  |  | Ying |  |  |  | FRC | Aircon too cold, make it warm-Su-low
FID5181 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 8 > Ward 842 (Ophir Suite) |  | 2021-12-30 10:54:51 | 2021-12-31 11:03:18 | 2021-12-31 11:03:41 | 2021-12-31 11:04:01 | 2021-12-31 11:04:22 | 2021-12-31 11:04:54 | Checked and repaired the call bell | [8 empty] | FRC | Call bell not working-senthil-low
FID5180 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 11 > Room 1126 (HR) |  | 2021-12-30 10:42:13 | 2021-12-31 11:00:12 | 2021-12-31 11:00:35 | 2021-12-31 11:01:03 | 2021-12-31 11:01:28 | 2021-12-31 11:02:39 | Checked and found it is due to floor trap choke. Cleared the floor trap choke, basin water flow as per normal | [8 empty] | FRC | Basin water flow very slow-Hossain-low
FID5179 | Plumbing & Sanitary | Basin / sink | Other: Scrub sink no power | Affecting Public | RMG > RH > 7 > OR7&8 Scrub Rm |  | 2021-12-30 10:38:39 | 2021-12-31 10:57:28 | 2021-12-31 10:57:49 | 2021-12-31 10:58:13 | 2021-12-31 10:58:40 | 2021-12-31 10:59:27 | Checked and found there is power trip. Reset the power, back to normal |  |  |  |  | Sister chew |  |  |  | FRC | Scrub sink no power-Shanmu-low
FID5178 | Plumbing & Sanitary | Floor trap | Choked | Affecting Public | RMG > RH > 9 > Stn C Pantry |  | 2021-12-30 10:36:57 | 2021-12-30 10:40:16 | 2021-12-31 10:55:32 | 2021-12-31 10:55:53 | 2021-12-31 10:56:18 | 2021-12-31 10:56:46 | Cleared the choke | [8 empty] | FRC | Floor trap choke-Hossain-low
FID5177 | Medical Equipment | Fridges & Freezers | Alarm | Localised to room | RMG > RH > 7 > OT Clean Corridor |  | 2021-12-30 10:30:55 | 2021-12-31 10:45:08 | 2021-12-31 10:48:31 | 2021-12-31 10:48:52 | 2021-12-31 10:49:15 | 2021-12-31 10:52:41 | Upon reaching onsite, freezer is working as per normal and temperature is in range. Informed to user. |  |  |  |  | Sister cherry |  |  |  | FRC | Ch 20 freezer alarming-Isyamudin-low
FID5176 | Office and Furniture | Telephone | Cannot operate / defective | Localised to room | RMG > RH > 7 > Day Surgery |  | 2021-12-30 10:16:58 | 2021-12-31 10:38:51 | 2021-12-31 10:40:49 | 2021-12-31 10:42:55 | 2021-12-31 10:43:18 | 2021-12-31 10:44:09 | Checked and found there is power trip. Reset the power back to normal | [8 empty] | FRC | IP phone no power-Senthil-low
FID5173 | Medical Equipment | Medical Gas | Change Cylinders | Affecting Public | RMG > RH > 1 > Nuclear Medicine Centre |  | 2021-12-30 09:48:12 | 2021-12-31 10:29:43 | 2021-12-31 10:32:12 | 2021-12-31 10:32:31 | 2021-12-31 10:37:34 | 2021-12-31 10:38:02 | Replaced new oxygen cylinder | [8 empty] | FRC | Need to replace 1 big portable oxygen cylinder for e trolley-Nazri-medium
FID5172 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > ICU |  | 2021-12-30 09:46:47 | 2021-12-30 17:27:30 | 2021-12-30 17:28:22 | 2021-12-30 17:28:47 | 2021-12-30 17:30:24 | 2021-12-30 17:37:14 | Collected 6 big oxygen cylinder and replaced 5 new cylinders | [8 empty] | FRC | Need to replace 5 big oxygen cylinders-Hossain-medium
FID5171 | Plumbing & Sanitary | WC / Squatting Pedestal | Water flowing non-stop | Affecting Public | RMG > RH > 9 > Stn A Soiled Utility Rm |  | 2021-12-30 09:45:41 | 2021-12-30 17:25:08 | 2021-12-30 17:25:33 | 2021-12-30 17:25:54 | 2021-12-30 17:26:16 | 2021-12-30 17:26:44 | Adjusted the flushing system |  |  |  |  | HK |  |  |  | FRC | Water non-stop flushing-nazri-low
FID5169 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 8 > Ward 809 |  | 2021-12-30 09:43:11 | 2021-12-30 17:22:47 | 2021-12-30 17:23:09 | 2021-12-30 17:23:31 | 2021-12-30 17:23:52 | 2021-12-30 17:24:22 | Cleared the basin choke | [8 empty] | FRC | Basin choke-nazri-low
FID5168 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 12 > Women Centre Consult Rm 22 |  | 2021-12-30 09:41:40 | 2021-12-30 17:20:27 | 2021-12-30 17:20:50 | 2021-12-30 17:21:16 | 2021-12-30 17:21:39 | 2021-12-30 17:22:05 | Replaced new light | [8 empty] | FRC | Light flickering-nazri-low
FID5167 | Office and Furniture | Printer | Cannot operate / defective | Localised to room | RMG > RH > 9 > Nursing Stn A |  | 2021-12-30 09:40:52 | 2021-12-30 16:11:04 | 2021-12-30 16:11:25 | 2021-12-30 17:07:33 | 2021-12-30 17:07:56 | 2021-12-30 17:08:34 | Checked and found printer not connecting to computer. Informed staff to report to IT dept |  |  |  |  | staff |  |  |  | FRC | Printer not working-satha-low
FID5165 | Office and Furniture | TV | Cannot operate / defective | Localised to room | RMG > RH > 10 > Ward 1049 |  | 2021-12-30 09:38:20 | 2021-12-30 09:45:06 | 2021-12-30 09:45:42 | 2021-12-30 09:46:55 | 2021-12-30 09:47:26 | 2021-12-30 09:49:08 | reset the power then back to normal | [8 empty] | FRC | TV not working-ilayaraja-low
FID5162 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-30 07:59:56 | 2021-12-30 08:00:52 | 2021-12-30 08:01:18 | 2021-12-30 08:33:07 | 2021-12-30 08:33:43 | 2021-12-30 08:35:54 | aircon adjested to 26 then make it warm | [8 empty] | FRC | Aircon very cool, make warm to 24c-ilayaraja-low
FID5157 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1052 |  | 2021-12-29 20:10:49 | 2021-12-29 20:27:59 | 2021-12-29 20:28:33 | 2021-12-29 20:30:21 | 2021-12-29 20:32:40 | 2021-12-29 20:34:34 | room tamper position manually open 85 persent make it cool | [8 empty] | FRC | Aircon make it cool -Aru-low
FID5156 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1030 |  | 2021-12-29 20:06:53 | 2021-12-29 20:19:06 | 2021-12-29 20:19:41 | 2021-12-29 20:21:19 | 2021-12-29 20:23:20 | 2021-12-29 20:24:46 | aircon make it cool room tamper manually open in bms | [8 empty] | FRC | Aircon make it cool-Aru-low
FID5151 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > OT Doctor Changing Rm |  | 2021-12-29 17:35:59 | 2021-12-29 17:52:01 | 2021-12-29 17:52:43 | 2021-12-29 17:53:09 | 2021-12-29 17:53:38 | 2021-12-29 18:00:18 | Replaced new bulb | [8 empty] | FRC | Light fused -mani-low
FID5150 | Plumbing & Sanitary | Basin / sink | Leaking | Affecting Public | RMG > RH > 9 > Nursing Stn D |  | 2021-12-29 17:04:46 | 2021-12-29 17:33:00 | 2021-12-29 17:33:24 | 2021-12-29 17:33:48 | 2021-12-29 19:20:58 | 2021-12-29 19:21:42 | change new one | [8 empty] | FRC | Water leaking below the basin-ming cai-low
FID5149 | Mechanical | AHU / FCU / CU | Leaking / Condensation | Localised to room | RMG > RH > 1 > FCC |  | 2021-12-29 16:39:22 | 2021-12-30 10:07:28 | 2021-12-30 10:08:41 | 2021-12-30 10:09:05 | 2021-12-30 16:00:31 | 2021-12-30 16:04:03 | Drain pipe choke. Vacuumed the drain pipe and tray, aircon working back to normal |  |  |  |  | Mohan (FCC) |  |  |  | FRC | Aircon leaking-aru-low
FID5140 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 7 > ICU Rm 709 |  | 2021-12-29 15:23:13 | 2021-12-30 16:07:33 | 2021-12-30 16:08:28 | 2021-12-30 16:08:49 | 2021-12-30 16:09:16 | 2021-12-30 16:09:58 | Checked and repaired the call bell | [8 empty] | FRC | Call bell not working-senthil-low
FID5139 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 9 > Ward 969 - 970 |  | 2021-12-29 15:22:30 | 2021-12-29 15:24:06 | 2021-12-29 15:51:50 | 2021-12-29 15:52:22 | 2021-12-29 15:52:51 | 2021-12-29 15:54:17 | Reset normal back | [8 empty] | FRC | Call bell keep alarming -mani-low
FID5132 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 11 > Room 1126 (HR) |  | 2021-12-29 14:26:39 | 2021-12-30 10:02:51 | 2021-12-30 10:04:51 | 2021-12-30 10:05:31 | 2021-12-30 10:05:57 | 2021-12-30 10:06:29 | Cleared the basin choke | [8 empty] | FRC | Basin water flow very slow-nazri-low
FID5131 | Office and Furniture | TV | Other: TV remote not working | Affecting Public | RMG > RH > 10 > Ward 1065 |  | 2021-12-29 14:25:52 | 2021-12-29 15:12:25 | 2021-12-29 15:14:29 | 2021-12-29 15:17:21 | 2021-12-29 15:19:49 | 2021-12-29 15:22:02 | Replaced new battery | [8 empty] | FRC | TV remote not working -mani-low
FID5128 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1052 |  | 2021-12-29 13:46:14 | 2021-12-29 13:47:14 | 2021-12-29 13:47:37 | 2021-12-29 13:47:58 | 2021-12-29 13:48:20 | 2021-12-29 13:52:49 | Adjusted VAV 1-1-23 temperature setpoint from 24c to 26c and damper position from 10% to 5% manually in bms system make it warm | [8 empty] | FRC | Aircon make it warm-su-low
FID5127 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 11 > Room 1107 (QM) |  | 2021-12-29 13:38:54 | 2021-12-29 15:03:58 | 2021-12-29 15:06:20 | 2021-12-29 15:06:57 | 2021-12-29 15:07:45 | 2021-12-29 15:09:48 | Replaced new bulb |  |  |  |  | Shafie (QM) |  |  |  | FRC | Light fused -mani-low
FID5126 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Histo Data Rm |  | 2021-12-29 13:38:09 | 2021-12-30 09:59:00 | 2021-12-30 09:59:24 | 2021-12-30 09:59:48 | 2021-12-30 10:01:31 | 2021-12-30 10:02:04 | Adjusted the aircon make it warm |  |  |  |  | Kar Lai |  |  |  | FRC | Aircon make it warm-isyamudin-low
FID5125 | Mechanical | AHU / FCU / CU | Noisy | Affecting Public | RMG > RH > 9 > Business Centre Office 1 |  | 2021-12-29 13:37:01 | 2021-12-30 09:53:07 | 2021-12-30 09:55:55 | 2021-12-30 09:56:32 | 2021-12-30 09:57:12 | 2021-12-30 09:57:56 | Adjusted the damper manually onsite to reduce the airflow noise |  |  |  |  | mike |  |  |  | FRC | Sound coming from the aircon-aru-low
FID5124 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn C |  | 2021-12-29 13:33:42 | 2021-12-29 13:34:13 | 2021-12-29 13:35:01 | 2021-12-29 13:35:23 | 2021-12-29 13:35:44 | 2021-12-29 13:49:31 | Adjusted VAV 2-1-22 temperature setpoint from 24c to 22c in bms system make it cool. Damper position automatically increase from 20% to 75% | [8 empty] | FRC | Aircon make it cool-su-low
FID5122 | Office and Furniture | Cabinet | Cannot open / close | Localised to room | RMG > RH > 13 > Ward 13 |  | 2021-12-29 11:10:29 | 2021-12-29 14:49:10 | 2021-12-29 14:49:30 | 2021-12-29 14:49:51 | 2021-12-29 14:50:13 | 2021-12-29 14:51:05 | Staff key missing. Break opened the locker lock as per staff request. |  |  |  |  | Nurse Latifah |  |  |  | FRC | Need to open staff locker-Allan-low
FID5121 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1059 |  | 2021-12-29 11:03:56 | 2021-12-29 14:46:03 | 2021-12-29 14:46:25 | 2021-12-29 14:46:45 | 2021-12-29 14:47:07 | 2021-12-29 14:52:20 | Adjusted the room vav temperature setpoint and damper position in bms system make it warm | [8 empty] | FRC | Aircon make it warm -aru-low
FID5120 | Electrical | Call System | Other: Call bell keep ringing | Affecting Public | RMG > RH > 8 > Ward 842 (Ophir Suite) |  | 2021-12-29 11:02:07 | 2021-12-29 11:07:46 | 2021-12-29 11:08:19 | 2021-12-29 11:09:33 | 2021-12-29 11:09:45 | 2021-12-29 11:11:11 | Reset normal back | [8 empty] | FRC | Call bell keep ringing-mani-low
FID5118 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 1 > A&E Bed 1 & 2 |  | 2021-12-29 10:25:55 | 2021-12-29 10:28:26 | 2021-12-29 10:29:01 | 2021-12-29 10:31:35 | 2021-12-29 10:39:26 | 2021-12-29 10:43:59 | Replaced new bulb | [8 empty] | FRC | Light fused-mani-low
FID5116 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | Affecting Public | RMG > RH > 7 > Operating Theatre 2 (IVF) |  | 2021-12-29 09:51:14 | 2021-12-29 14:42:32 | 2021-12-29 14:42:53 | 2021-12-29 14:43:27 | 2021-12-29 14:43:50 | 2021-12-30 09:52:18 | Reduced the airflow onsite |  |  |  |  | Ying |  |  |  | FRC | Aircon too cold-aru-low
FID5115 | Medical Equipment | Patient Bed | Other: Cannot operate | Affecting Public | RMG > RH > 13 > Ward 1358-1363 |  | 2021-12-29 09:50:21 | 2021-12-29 10:05:47 | 2021-12-29 10:06:20 | 2021-12-29 10:06:55 | 2021-12-29 10:07:19 | 2021-12-29 10:10:56 | onsite check & found patient bed is not working due to mcb tripped. reset back the mcb back to normal. | [8 empty] | FRC | Bed cannot adjust-Hossain-low
FID5114 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 11 > CT Scan Room 25 |  | 2021-12-29 09:47:39 | 2021-12-29 14:35:12 | 2021-12-29 14:35:35 | 2021-12-29 14:36:11 | 2021-12-29 14:37:52 | 2021-12-30 09:51:22 | Checked and found AHU/L11/C/02 belt spoilt. Replaced new belts and checked the airflow in the room, back to normal. | [8 empty] | FRC | Aircon make it cool-Aru-low
FID5113 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 11 > U/S Rm 22 |  | 2021-12-29 09:46:54 | 2021-12-29 14:33:34 | 2021-12-29 14:33:55 | 2021-12-29 14:34:16 | 2021-12-29 14:34:36 | 2021-12-30 09:50:34 | Checked and found AHU/L11/C/02 belt spoilt. Replaced new belts and checked the airflow in the room, back to normal. | [8 empty] | FRC | Aircon make it cool-Aru-low
FID5112 | Electrical | Vending Machine | Unserviceable | Affecting Public | RMG > RSC > 9 > Internal Med |  | 2021-12-29 09:46:09 | 2021-12-29 14:30:20 | 2021-12-29 14:30:49 | 2021-12-29 14:31:25 | 2021-12-29 14:32:23 | 2021-12-29 14:32:55 | Restart the vending machine power, working back to normal | [8 empty] | FRC | Coffee machine (1160421) out of order-nazri-low
FID5111 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 9 > Nursing Stn B |  | 2021-12-29 09:41:53 | 2021-12-29 14:21:31 | 2021-12-29 14:22:22 | 2021-12-29 14:22:43 | 2021-12-29 14:23:06 | 2021-12-29 14:23:52 | Adjusted the temperature in bms system make it cool | [8 empty] | FRC | Aircon make it cool -satha-low
FID5110 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn C |  | 2021-12-29 09:40:59 | 2021-12-29 14:17:11 | 2021-12-29 14:17:53 | 2021-12-29 14:19:12 | 2021-12-29 14:19:32 | 2021-12-29 14:20:09 | Adjusted the vav temperature setpoint in bms system make it warm | [8 empty] | FRC | Aircon make it warm -satha-low
FID5104 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 7 > ICU Counter A |  | 2021-12-29 07:30:30 | 2021-12-29 07:35:57 | 2021-12-29 07:36:41 | 2021-12-29 08:13:14 | 2021-12-29 08:15:25 | 2021-12-29 08:17:09 | replaced the new light |  |  |  |  | staff from icu |  |  |  | FRC | Light flickering-ilayaraja-low
FID5103 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 817 |  | 2021-12-29 07:28:10 | 2021-12-29 07:32:01 | 2021-12-29 07:32:23 | 2021-12-29 07:32:44 | 2021-12-29 07:33:07 | 2021-12-29 07:34:54 | close diffuser control airflow |  |  |  |  | staff from 8b |  |  |  | FRC | Aircon make it warm-satha-low
FID5102 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1009 |  | 2021-12-28 22:47:07 | 2021-12-28 22:47:44 | 2021-12-28 22:48:07 | 2021-12-28 22:48:36 | 2021-12-28 22:48:59 | 2021-12-28 22:50:29 | damper position set at 5 percent manually change to auto |  |  |  |  | staff from 10 B |  |  |  | FRC | Aircon make cool-satha-low
FID5101 | Medical Equipment | Fridges & Freezers | Leaking | Localised to room | RMG > RH > 8 > Ward 817 |  | 2021-12-28 22:44:57 | 2021-12-28 22:46:40 | 2021-12-28 23:02:36 | 2021-12-28 23:03:00 | 2021-12-28 23:04:02 | 2021-12-28 23:05:10 | clear the water and checked compressor running normal . change the setting to cool position |  |  |  |  | staff from 8b |  |  |  | FRC | Fridge leaking-satha-low
FID5100 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 8 > Ward 810 |  | 2021-12-28 20:41:32 | 2021-12-29 13:56:23 | 2021-12-29 13:56:43 | 2021-12-29 13:57:02 | 2021-12-29 13:57:22 | 2021-12-29 13:58:44 | change battery | [8 empty] | FRC | Need to change wall clock battery-ming cai-low
FID5095 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1319-1327 |  | 2021-12-28 19:05:43 | 2021-12-28 19:06:39 | 2021-12-28 19:07:24 | 2021-12-28 19:08:11 | 2021-12-28 19:08:40 | 2021-12-28 19:16:25 | adjusted vav 1-1-10 damper position from 20%to5% in bms system make it warm | [8 empty] | FRC | Aircon make it warm -mani-low
FID5094 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 8 > Ward 842 (Ophir Suite) |  | 2021-12-28 17:46:23 | 2021-12-29 14:06:05 | 2021-12-29 14:07:22 | 2021-12-29 14:07:45 | 2021-12-29 14:09:09 | 2021-12-29 14:12:31 | Opened the diffuser manually onsite | [8 empty] | FRC | Aircon make it cool-Isyamudin-low
FID5091 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 842 (Ophir Suite) |  | 2021-12-28 17:04:38 | 2021-12-28 17:05:05 | 2021-12-28 17:05:31 | 2021-12-28 17:05:56 | 2021-12-28 17:06:20 | 2021-12-28 17:47:37 | Staff told not to come onsite to check and adjust in bms. So adjusted the temperature setpoint for the isolation room from 19c to 17c and heater set to 0% manual in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5090 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1030 |  | 2021-12-28 16:49:59 | 2021-12-28 16:50:40 | 2021-12-28 16:51:08 | 2021-12-28 16:51:33 | 2021-12-28 16:51:55 | 2021-12-28 17:00:52 | Adjusted VAV 2-3-6 damper position from 20% to 5% in bms system make it warm. Thermostat setting at 29.5c | [8 empty] | FRC | Aircon make it warm-su-low
FID5089 | Electrical | Call System | Other: Call bell keep ringing | Affecting Public | RMG > RH > 8 > Ward 842 (Ophir Suite) |  | 2021-12-28 16:49:09 | 2021-12-28 17:31:17 | 2021-12-28 17:33:46 | 2021-12-28 18:07:37 | 2021-12-28 18:08:12 | 2021-12-29 14:04:52 | Checked and rectified | [8 empty] | FRC | Call bell keep ringing non stop-a.bala-low
FID5088 | Office and Furniture | Patient Bed | Cannot operate / defective | Affecting Public | RMG > RH > 7 > ICU Rm 708 |  | 2021-12-28 16:48:13 | 2021-12-29 14:13:11 | 2021-12-29 14:13:26 | 2021-12-29 14:13:41 | 2021-12-29 14:14:17 | 2021-12-29 14:16:10 | Bed part missing. Replaced new part | [8 empty] | FRC | Bed cannot adjust-ming cai-low
FID5087 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 11 > Room 1102 (IT) |  | 2021-12-28 16:17:39 | 2021-12-28 16:29:17 | 2021-12-28 16:30:45 | 2021-12-28 16:32:14 | 2021-12-28 16:33:18 | 2021-12-28 16:34:20 | Replaced new bulb |  |  |  |  | Jia Jing |  |  |  | FRC | Light fused-mani-low
FID5086 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 7 > Handicap Toilet 1 |  | 2021-12-28 16:06:55 | 2021-12-29 14:01:10 | 2021-12-29 14:01:31 | 2021-12-29 14:01:53 | 2021-12-29 14:03:34 | 2021-12-29 14:04:00 | Cleared the basin choke | [8 empty] | FRC | Basin choke-nazri-low
FID5077 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-28 14:48:40 | 2021-12-28 14:49:31 | 2021-12-28 14:49:56 | 2021-12-28 14:50:20 | 2021-12-28 14:50:45 | 2021-12-28 15:18:13 | Adjusted the heater from 100% manual to 0% manual in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5075 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn D |  | 2021-12-28 14:34:22 | 2021-12-28 14:39:09 | 2021-12-28 14:39:31 | 2021-12-28 14:40:26 | 2021-12-28 14:40:49 | 2021-12-28 15:16:38 | Adjusted VAV 1-1-13 temperature setpoint from 24c to 22c in bms system make it cool. Damper position increase from 20% to 51% | [8 empty] | FRC | Aircon make it cool-su-low
FID5074 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > ICU Counter A |  | 2021-12-28 14:32:37 | 2021-12-28 14:37:07 | 2021-12-28 14:37:32 | 2021-12-28 14:38:16 | 2021-12-28 14:38:40 | 2021-12-28 15:29:12 | Adjusted the temperature setpoint in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5073 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn B |  | 2021-12-28 14:30:59 | 2021-12-28 14:34:46 | 2021-12-28 14:35:05 | 2021-12-28 14:35:30 | 2021-12-28 14:36:20 | 2021-12-28 15:28:39 | Adjusted the temperature setpoint in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID5072 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RSC > 8 > ENT |  | 2021-12-28 14:26:10 | 2021-12-28 16:36:41 | 2021-12-28 16:37:28 | 2021-12-28 16:38:01 | 2021-12-28 16:38:32 | 2021-12-28 16:40:24 | Replaced new bulb | [8 empty] | FRC | Light fused-mani-low
FID5071 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 10 > Ward 1021 |  | 2021-12-28 14:20:17 | 2021-12-29 13:58:47 | 2021-12-29 13:59:07 | 2021-12-29 13:59:28 | 2021-12-29 13:59:49 | 2021-12-29 14:00:18 | Replaced new wall clock battery |  |  |  |  | Jasmine (HK) |  |  |  | FRC | Need to replace wall clock battery-Hossain-low
FID5069 | Plumbing & Sanitary | WC / Squatting Pedestal | Other: Flush not working | Affecting Public | RMG > RH > 2 > Raffles Japanese Clinic |  | 2021-12-28 13:49:17 | 2021-12-28 14:18:08 | 2021-12-28 14:18:33 | 2021-12-28 14:20:04 | 2021-12-28 14:20:27 | 2021-12-28 14:21:14 | clear up | [8 empty] | FRC | Toilet flush not working-ming cai-low
FID5065 | Electrical | Light Bulb | Misaligned / dangling | Affecting Public | RMG > RH > 1 > A&E Waiting Area |  | 2021-12-28 11:01:42 | 2021-12-29 11:16:38 | 2021-12-29 11:26:03 | 2021-12-29 11:29:24 | 2021-12-29 11:29:45 | 2021-12-29 11:30:16 | Fixed back the signage and secure properly | [8 empty] | FRC | Exit light signage going to drop-Senthil-low
FID5064 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 7 > ICU Rm 705 |  | 2021-12-28 11:00:53 | 2021-12-28 11:22:10 | 2021-12-28 11:32:26 | 2021-12-28 11:33:03 | 2021-12-28 11:33:47 | 2021-12-28 11:34:25 | Reset normal back | [8 empty] | FRC | Call bell not working-mani-low
FID5063 | Building | Door Closer | Noisy | Affecting Public | RMG > RSC > 11 > X-Ray Control 27 |  | 2021-12-28 10:56:37 | 2021-12-28 11:19:57 | 2021-12-28 11:20:19 | 2021-12-28 11:20:53 | 2021-12-28 11:21:12 | 2021-12-28 11:22:11 | The door no more noisy we do it |  |  |  |  | Abu (HK) |  |  |  | FRC | Door noisy when opening and closing - Allan-low
FID5062 | Plumbing & Sanitary | WC / Squatting Pedestal | Other: Toilet seat cover come out | Localised to room | RMG > RH > 13 > Ward 1319-1327 |  | 2021-12-28 10:51:26 | 2021-12-29 10:48:52 | 2021-12-29 10:50:26 | 2021-12-29 10:50:51 | 2021-12-29 10:51:15 | 2021-12-29 10:51:46 | Fixed and tighten back the toilet seat cover | [8 empty] | FRC | Toilet seat cover come out-Nazri-low
FID5061 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 7 |  | 2021-12-28 10:47:35 | 2021-12-28 10:47:58 | 2021-12-28 10:48:24 | 2021-12-28 10:48:43 | 2021-12-28 10:49:04 | 2021-12-29 10:53:43 | Open the vav damper and grill fully onsite to allow more airflow |  |  |  |  | Siti |  |  |  | FRC | Aircon make it cool-Isyamudin-low
FID5060 | Medical Equipment | Fridges & Freezers | Other: Fridge showing high temperature | Localised to room | RMG > RH > 8 > Nursing Stn B |  | 2021-12-28 10:45:09 | 2021-12-29 10:54:21 | 2021-12-29 11:04:33 | 2021-12-29 11:04:53 | 2021-12-29 11:05:52 | 2021-12-29 11:06:31 | Adjusted the fridge settings back to normal |  |  |  |  | Staff |  |  |  | FRC | Fridge temperature high-Aru-low
FID5059 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 11 > U/S Rm 22 |  | 2021-12-28 10:41:54 | 2021-12-29 13:56:05 | 2021-12-29 13:56:27 | 2021-12-29 13:56:48 | 2021-12-29 13:57:09 | 2021-12-29 13:57:29 | Adjusted the temperature setpoint in bms system make it cool |  |  |  |  | Cynthia |  |  |  | FRC | Aircon make it cool-aru-low
FID5058 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 11 > U/S Rm 21 |  | 2021-12-28 10:41:16 | 2021-12-29 13:53:42 | 2021-12-29 13:54:03 | 2021-12-29 13:54:25 | 2021-12-29 13:54:56 | 2021-12-29 13:55:21 | Adjusted the temperature setpoint in bms system make it cool | [8 empty] | FRC | Aircon make it cool-aru-low
FID5057 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 11 > U/S Rm 17 |  | 2021-12-28 10:39:18 | 2021-12-29 13:41:54 | 2021-12-29 13:42:15 | 2021-12-29 13:42:37 | 2021-12-29 13:42:58 | 2021-12-29 13:43:30 | Adjusted the temperature setpoint in bms system make it cool |  |  |  |  | Cynthia |  |  |  | FRC | Aircon make it cool-aru-low
FID5056 | Building | Door Frame | Other: Need to shift the signage | Localised to room | RMG > RH > 10 > Nursing Stn C |  | 2021-12-28 10:35:26 | 2021-12-28 18:51:10 | 2021-12-28 18:51:31 | 2021-12-28 18:51:51 | 2021-12-28 18:52:11 | 2021-12-28 18:52:41 | I have change the signboard |  |  |  |  | Felix |  |  |  | FRC | Need to shift the signage to be placed directly above glass vision panel on the door-allan-low
FID5055 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Localised to room | RMG > RH > 13 > Ward 1319-1327 |  | 2021-12-28 10:33:44 | 2021-12-29 10:42:26 | 2021-12-29 10:44:48 | 2021-12-29 10:45:12 | 2021-12-29 10:45:37 | 2021-12-29 10:46:18 | Bidet spray faulty, replaced new bidet spray |  |  |  |  | Housekeeping |  |  |  | FRC | Bidet spray non-stop spraying-Nazri-low
FID5054 | Office and Furniture | TV | Other: TV remote not working | Localised to room | RMG > RH > 10 > Ward 1048 |  | 2021-12-28 10:32:17 | 2021-12-29 10:20:34 | 2021-12-29 10:20:54 | 2021-12-29 10:21:15 | 2021-12-29 10:21:35 | 2021-12-29 10:23:24 | Replaced new battery for tv remote | [8 empty] | FRC | TV remote not working -a.bala-low
FID5053 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 11 > U/S Rm 11 |  | 2021-12-28 10:21:32 | 2021-12-29 10:38:41 | 2021-12-29 10:39:13 | 2021-12-29 10:39:38 | 2021-12-29 10:40:02 | 2021-12-29 10:40:40 | Adjusted the room vav temperature setpoint in bms system make it cool |  |  |  |  | Cynthia |  |  |  | FRC | Aircon make it cool-aru-low
FID5051 | Medical Equipment | Fridges & Freezers | Other: Fridge showing high temperature | Affecting Public | RMG > RH > 8 > Nursing Stn D |  | 2021-12-28 10:11:06 | 2021-12-29 09:52:14 | 2021-12-29 09:52:33 | 2021-12-29 09:53:21 | 2021-12-29 09:53:41 | 2021-12-29 09:54:24 | Checked on site, fridge temperature within range. Informed to staff | [8 empty] | FRC | Fridge showing high temperature-V.bala-low
FID5050 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 12 > Raffles Health Screeners |  | 2021-12-28 10:04:39 | 2021-12-29 09:55:03 | 2021-12-29 09:55:24 | 2021-12-29 09:55:47 | 2021-12-29 09:56:08 | 2021-12-29 09:57:10 | Adjusted AHU 12-2 cooling valve from 60% manual to auto in bms system make it warm |  |  |  |  | Farah |  |  |  | FRC | Aircon too cold, make it warm-Isyamudin-low
FID5040 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 2 > Skin & Aesthetics Consult Rm 6 |  | 2021-12-28 08:37:12 | 2021-12-29 10:00:47 | 2021-12-29 10:02:13 | 2021-12-29 10:02:42 | 2021-12-29 10:03:02 | 2021-12-29 10:04:02 | Adjusted the room vav temperature setpoint in bms system make it cool | [8 empty] | FRC | Aircon make it cool-v.bala-low
FID5039 | Office and Furniture | Patient Bed | Chipped / Cracked | More than 1 room | RMG > RH > 1 > A&E Bed 7 & 8 |  | 2021-12-28 08:33:25 | 2021-12-29 10:05:09 | 2021-12-29 10:05:29 | 2021-12-29 10:05:45 | 2021-12-29 10:06:00 | 2021-12-29 10:06:51 | Bed side rail broken. Unable to fix. Pending follow-up | [8 empty] | FRC | Bed handle broken-v.bala-low
FID5038 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 9 > Nursing Stn A |  | 2021-12-28 07:46:01 | 2021-12-28 07:47:14 | 2021-12-28 07:49:18 | 2021-12-28 07:51:07 | 2021-12-28 07:55:23 | 2021-12-28 08:02:37 | replaced new light bulb | [8 empty] | FRC | Light fused-A.Bala-low
FID5037 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > Operating Theatre 9 |  | 2021-12-28 07:32:55 | 2021-12-28 07:33:20 | 2021-12-28 07:33:49 | 2021-12-28 07:34:32 | 2021-12-28 07:35:02 | 2021-12-28 07:36:25 | adjusted the temprature make it cold | [8 empty] | FRC | Aircon warm, make it cold-A.Bala-low
FID5035 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU Rm 710 |  | 2021-12-27 19:38:23 | 2021-12-27 19:38:58 | 2021-12-27 19:40:10 | 2021-12-27 19:42:10 | 2021-12-27 19:44:06 | 2021-12-27 19:45:09 | adjusted the setpoint in thermostat |  |  |  |  | staff from icu |  |  |  | FRC | Aircon make cool-satha-low
FID5034 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 4 > Carpark |  | 2021-12-27 19:16:41 | 2021-12-27 19:17:13 | 2021-12-27 19:18:41 | 2021-12-27 19:19:11 | 2021-12-27 19:19:35 | 2021-12-27 19:20:26 | replace new light |  |  |  |  | staff |  |  |  | FRC | Carpark lot 217 light flickering-satha-low
FID5033 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 6 |  | 2021-12-27 19:10:05 | 2021-12-27 19:11:42 | 2021-12-27 19:12:46 | 2021-12-27 19:13:33 | 2021-12-27 19:14:36 | 2021-12-27 19:15:12 | deactive heater | [8 empty] | FRC | Aircon make cool-satha-low
FID5032 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 11 > Facilities Dept. |  | 2021-12-27 19:08:47 | 2021-12-27 19:16:12 | 2021-12-27 19:25:23 | 2021-12-27 19:26:11 | 2021-12-27 19:27:22 | 2021-12-27 19:28:40 | replace light |  |  |  |  | Pei Yu |  |  |  | FRC | Light blown-satha-low
FID5031 | Office and Furniture | Cabinet | Other: Need to remove wheel | Affecting Public | RMG > RH > 12 > Raffles Executive Medical Centre |  | 2021-12-27 16:54:33 | 2021-12-27 17:10:25 | 2021-12-27 17:11:20 | 2021-12-27 17:12:04 | 2021-12-27 17:23:55 | 2021-12-27 17:25:51 | removed the capinet whee . |  |  |  |  | Gerrand |  |  |  | FRC | Need to remove pedestal wheel-ilayaraja-low
FID5030 | Mechanical | AHU / FCU / CU | Other: Hygrometer | Localised to room | RMG > RH > 10 > Ward 1046 (Pharmacy Store) |  | 2021-12-27 16:50:48 | 2021-12-27 17:03:40 | 2021-12-27 17:04:14 | 2021-12-27 17:05:19 | 2021-12-27 17:06:16 | 2021-12-27 17:07:37 | replaced new battery after normal | [8 empty] | FRC | Need to replace hygrometer battery-Isyamudin-low
FID5027 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 4 |  | 2021-12-27 16:34:55 | 2021-12-27 16:35:19 | 2021-12-27 16:35:39 | 2021-12-27 16:36:00 | 2021-12-27 16:36:32 | 2021-12-27 16:47:30 | Adjusted the temperature setpoint from 28c to 22c and heater from 50% manual to auto in bms system make it cool. | [8 empty] | FRC | Aircon make it cool-su-low
FID5020 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RSC > 11 > U/S Rm 13 |  | 2021-12-27 16:20:02 | 2021-12-28 14:17:05 | 2021-12-28 14:17:30 | 2021-12-28 14:17:54 | 2021-12-28 14:18:14 | 2021-12-28 14:19:15 | Adjusted VAV 11-1-2 temperature setpoint from 23c to 19c and damper from auto (50%) to 80% manual in bms system make it cool | [8 empty] | FRC | Aircon warm-Aru-low
FID5015 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RSC > 16 > Staircase 5 |  | 2021-12-27 14:57:04 | 2021-12-27 15:21:43 | 2021-12-27 15:22:18 | 2021-12-27 15:22:58 | 2021-12-27 15:23:25 | 2021-12-27 15:27:51 | Replaced new bulb |  |  |  |  | Naing (HK) |  |  |  | FRC | Light fused-mani-low
FID5013 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-27 14:34:11 | 2021-12-27 14:34:42 | 2021-12-27 14:35:01 | 2021-12-27 14:35:22 | 2021-12-27 14:36:28 | 2021-12-27 14:43:12 | Adjusted the temperature setpoint from 22c to 18c and heater from 100% to 0% manual in bms system make cool | [8 empty] | FRC | Aircon make it cool to 19c, now showing 21.3c-Su-low
FID5012 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 10 |  | 2021-12-27 13:59:08 | 2021-12-27 13:59:30 | 2021-12-27 14:00:10 | 2021-12-27 14:00:35 | 2021-12-27 14:00:55 | 2021-12-27 14:02:13 | Adjusted the temperature setpoint from 22c to 18c and heater from 100% manual to 0% manual make it cool in bms system | [8 empty] | FRC | Aircon make it cool to 18c, now showing 25c-Su-low
FID5010 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 2 > Raffles Chinese Medicine Clinic |  | 2021-12-27 13:29:15 | 2021-12-27 13:29:37 | 2021-12-27 13:30:06 | 2021-12-27 13:30:30 | 2021-12-27 13:30:51 | 2021-12-27 13:35:47 | Adjusted the vav 5-2-16 temperature setpoint from 24c to 22c in bms system, make it cool. Damper position automatically increase from 20% to 82.5%. | [8 empty] | FRC | Aircon very stuffy-Su-low
FID5008 | Office and Furniture | Telephone | Cannot operate / defective | Localised to room | RMG > RH > 9 > Nursing Stn A |  | 2021-12-27 12:01:43 | 2021-12-27 12:08:11 | 2021-12-27 12:08:48 | 2021-12-27 12:09:08 | 2021-12-27 12:09:22 | 2021-12-27 12:11:42 | wire loose and normal back | [8 empty] | FRC | Telephone not working-mani-low
FID5007 | Medical Equipment | Fridges & Freezers | Other: Testo data logger | Localised to room | RMG > RSC > 11 > CT Scan Room 25 |  | 2021-12-27 11:50:26 | 2021-12-28 14:13:35 | 2021-12-28 14:13:56 | 2021-12-28 14:14:21 | 2021-12-28 14:14:42 | 2021-12-28 14:15:15 | Reset the data logger settings back to normal | [8 empty] | FRC | Testo data logger not recording-aru-low
FID5004 | Plumbing & Sanitary | Urinal | Choked | Localised to room | RMG > RH > 7 > OT Doctor Changing Rm |  | 2021-12-27 11:39:26 | 2021-12-27 11:58:18 | 2021-12-27 11:59:06 | 2021-12-27 11:59:30 | 2021-12-27 11:59:57 | 2021-12-27 12:00:31 | Cleared the choke |  |  |  |  | Sister Chew |  |  |  | FRC | Urinal choke-Hossain-low
FID4991 | Mechanical | Air Handling Unit | Other: Hygrometer | Localised to room | RMG > RH > 7 > Angio Technical / Store Rm |  | 2021-12-27 10:04:03 | 2021-12-28 14:10:32 | 2021-12-28 14:11:39 | 2021-12-28 14:11:59 | 2021-12-28 14:12:21 | 2021-12-28 14:12:52 | Replaced new hygrometer battery | [8 empty] | FRC | Need to replace hygrometer battery-Aru-low
FID4988 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn C |  | 2021-12-27 09:59:15 | 2021-12-27 10:16:41 | 2021-12-27 10:17:01 | 2021-12-27 10:17:20 | 2021-12-27 10:17:40 | 2021-12-27 10:19:16 | Adjusted VAV 2-1-22 temperature setpoint from 24c to 22c and damper position from 90% manual to 100% manual in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID4987 | Plumbing & Sanitary | Shower Fittings | Damaged / Loose / Cracked | Localised to room | RMG > RH > 7 > OT Male Channing Rm |  | 2021-12-27 09:48:12 | 2021-12-27 09:51:41 | 2021-12-27 09:52:01 | 2021-12-27 09:52:20 | 2021-12-27 09:52:38 | 2021-12-27 10:46:03 | Replaced new shower head |  |  |  |  | Satha |  |  |  | FRC | Shower head faulty-Hossain-low
FID4983 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 11 > Facilities Dept. |  | 2021-12-27 09:44:59 | 2021-12-27 09:49:25 | 2021-12-27 09:49:59 | 2021-12-27 09:50:21 | 2021-12-27 09:51:00 | 2021-12-27 10:05:33 | Replaced new bulb | [8 empty] | FRC | Light flickering -mani-low
FID4979 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-27 08:59:35 | 2021-12-27 09:03:32 | 2021-12-27 09:34:12 | 2021-12-27 09:34:44 | 2021-12-27 09:35:21 | 2021-12-27 09:36:27 | replaced co2 big 2 | [8 empty] | FRC | Need to replace 2 big CO2 cylinder-v.bala-medium
FID4978 | Electrical | Queue System | Unserviceable | More than 1 room | RMG > RH > 2 > RM@RH Counter |  | 2021-12-27 08:58:03 | 2021-12-27 08:58:59 | 2021-12-27 08:59:25 | 2021-12-27 08:59:47 | 2021-12-27 09:03:34 | 2021-12-27 09:14:27 | reset back to mormal | [8 empty] | FRC | Queue system not working-A.Bala-low
FID4974 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | More than 1 room | RMG > RH > 10 > Ward 1067 |  | 2021-12-26 23:58:31 | 2021-12-27 00:02:31 | 2021-12-27 00:02:54 | 2021-12-27 00:03:18 | 2021-12-27 00:03:43 | 2021-12-27 00:04:18 | Toilet bowl choke cleared | [8 empty] | FRC | Toilet choke-v.bala-low
FID4964 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn B |  | 2021-12-26 13:53:54 | 2021-12-26 13:54:53 | 2021-12-26 13:55:24 | 2021-12-26 13:55:50 | 2021-12-26 13:57:00 | 2021-12-26 13:57:36 | adjusted the setpoint to 22 degrees |  |  |  |  | staff from 10 B |  |  |  | FRC | Aircon make cool-satha-low
FID4962 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-26 12:18:38 | 2021-12-26 12:21:00 | 2021-12-26 12:21:39 | 2021-12-26 12:22:00 | 2021-12-26 12:23:51 | 2021-12-26 12:24:26 | change the setting to auto |  |  |  |  | staff ward 10 d |  |  |  | FRC | Aircon make cool-satha-low
FID4961 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Localised to room | RMG > RH > 8 > Delivery Suite 6 |  | 2021-12-26 12:17:06 | 2021-12-28 14:07:31 | 2021-12-28 14:07:51 | 2021-12-28 14:08:11 | 2021-12-28 14:08:31 | 2021-12-28 14:09:42 | Replaced new bidet spray |  |  |  |  | staff from delivery ward |  |  |  | FRC | Toilet spray leaking-ming cai-low
FID4956 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1328-1336 |  | 2021-12-26 07:21:25 | 2021-12-26 07:21:48 | 2021-12-26 07:22:10 | 2021-12-26 07:22:36 | 2021-12-26 07:22:58 | 2021-12-26 07:29:44 | adjusted the temperature setpoint 20c to 24c and manually in pms the system make it warm | [8 empty] | FRC | Aircon make it warm-mani-low
FID4954 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1358-1363 |  | 2021-12-25 23:12:19 | 2021-12-28 14:03:07 | 2021-12-28 14:05:23 | 2021-12-28 14:05:48 | 2021-12-28 14:06:10 | 2021-12-28 14:06:54 | Adjusted the temperature in bms system make it cool | [8 empty] | FRC | Aircon make it cool -aru-low
FID4947 | Plumbing & Sanitary | Basin / sink | Choked | More than 1 room | RMG > RH > 10 > Ward 1029 |  | 2021-12-25 16:47:52 | 2021-12-28 14:00:31 | 2021-12-28 14:01:04 | 2021-12-28 14:01:26 | 2021-12-28 14:01:48 | 2021-12-28 14:02:18 | Cleared the choke | [8 empty] | FRC | Basin choke -nazri-low
FID4946 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | More than 1 room | RMG > RSC > 2 > Male Toilet |  | 2021-12-25 15:39:10 | 2021-12-28 13:56:26 | 2021-12-28 13:58:14 | 2021-12-28 13:58:35 | 2021-12-28 13:58:58 | 2021-12-28 13:59:34 | Cleared the choke | [8 empty] | FRC | Toilet bowl choke-V.Bala-low
FID4944 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 850 |  | 2021-12-25 14:53:27 | 2021-12-25 14:54:13 | 2021-12-25 14:54:35 | 2021-12-25 14:55:00 | 2021-12-25 14:55:24 | 2021-12-25 14:57:02 | manually closed diffuser make it warm | [8 empty] | FRC | Aircon too cold, make it warm-V.bala-low
FID4943 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 1 > A&E Main Counter |  | 2021-12-25 14:39:35 | 2021-12-25 14:58:04 | 2021-12-25 14:58:31 | 2021-12-25 14:58:56 | 2021-12-25 14:59:21 | 2021-12-25 15:02:03 | adjusted the temperature in bms setpoint 24to22 degree | [8 empty] | FRC | Aircon warm, make it cool-V.Bala-low
FID4942 | Office and Furniture | Cabinet | Cannot open / close | More than 1 room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-25 13:52:18 | 2021-12-25 14:29:36 | 2021-12-25 14:30:01 | 2021-12-25 14:30:27 | 2021-12-25 14:39:34 | 2021-12-25 14:42:04 | inside paper dropped clear | [8 empty] | FRC | Drawer cannot close-V.bala-low
FID4936 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 9 > Nursing Stn A |  | 2021-12-25 10:04:48 | 2021-12-25 10:11:44 | 2021-12-25 10:12:16 | 2021-12-25 10:12:45 | 2021-12-25 10:13:20 | 2021-12-25 10:14:22 | Replaced new light bulb | [8 empty] | FRC | Light flickering -A.Bala-low
FID4932 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RSC > 1 > Male Toilet |  | 2021-12-25 07:56:05 | 2021-12-25 07:56:47 | 2021-12-25 07:57:13 | 2021-12-25 08:03:01 | 2021-12-25 08:03:34 | 2021-12-25 08:06:42 | choke clearly | [8 empty] | FRC | Toilet bowl choke-mani-low
FID4931 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 850 |  | 2021-12-25 07:48:39 | 2021-12-28 13:53:21 | 2021-12-28 13:53:43 | 2021-12-28 13:54:05 | 2021-12-28 13:54:26 | 2021-12-28 13:54:59 | Adjusted the diffuser manually onsite to make warm | [8 empty] | FRC | Aircon make it warm -aru-low
FID4930 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 10 > Doctor's Lounge |  | 2021-12-24 19:55:50 | 2021-12-24 20:55:24 | 2021-12-24 20:55:53 | 2021-12-24 20:57:11 | 2021-12-24 20:58:37 | 2021-12-24 21:00:00 | replaced new light bulb | [8 empty] | FRC | Light flickering -A.Bala-low
FID4925 | Plumbing & Sanitary | Urinal | Choked | Localised to room | RMG > RSC > 1 > Male Toilet |  | 2021-12-24 16:13:18 | 2021-12-24 16:14:13 | 2021-12-24 16:14:37 | 2021-12-24 16:15:03 | 2021-12-24 16:15:45 | 2021-12-24 16:16:33 | choke cleared | [8 empty] | FRC | Urinal bowl choke-v.bala-low
FID4923 | Plumbing & Sanitary | Basin / sink | Leaking | Localised to room | RMG > RH > 9 > Ward 969 - 970 |  | 2021-12-24 15:30:37 | 2021-12-24 17:06:04 | 2021-12-24 17:06:29 | 2021-12-24 17:06:54 | 2021-12-24 17:07:15 | 2021-12-24 17:08:00 | Water leaking gun | [8 empty] | FRC | Basin leaking-allan-low
FID4922 | Building | Wall Skirting | Misaligned / dangling | Localised to room | RMG > RH > 13 > Ward 1358-1363 |  | 2021-12-24 15:13:41 | 2021-12-27 11:33:31 | 2021-12-27 11:33:55 | 2021-12-27 11:35:03 | 2021-12-27 11:35:52 | 2021-12-27 11:36:25 | Fixed back the curtain | [8 empty] | FRC | Curtain dropped-nazri-low
FID4916 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 12 > RHS RM 26 |  | 2021-12-24 11:51:53 | 2021-12-24 11:52:35 | 2021-12-24 12:03:15 | 2021-12-24 12:11:31 | 2021-12-24 12:11:48 | 2021-12-24 12:12:52 | replaced new bulb | [8 empty] | FRC | Light flickering-Senthil-low
FID4914 | Mechanical | Autodoor | Misaligned / dangling | More than 1 room | RMG > RH > 1 > A&E |  | 2021-12-24 11:33:28 | 2021-12-24 11:34:41 | 2021-12-24 12:13:42 | 2021-12-24 12:14:00 | 2021-12-24 12:14:24 | 2021-12-24 12:15:06 | tighten screw | [8 empty] | FRC | Auto door cover dropped-Senthil-low
FID4913 | Plumbing & Sanitary | Flush Button | Water flowing non-stop | More than 1 room | RMG > RH > 9 > Ward 901 |  | 2021-12-24 11:10:04 | 2021-12-24 11:33:38 | 2021-12-24 11:33:59 | 2021-12-24 11:34:32 | 2021-12-24 11:34:53 | 2021-12-24 11:35:41 | fix | [8 empty] | FRC | Toilet flush water non stop-nazri-low
FID4912 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 2 > RM@RH |  | 2021-12-24 11:05:32 | 2021-12-24 11:11:15 | 2021-12-24 11:12:00 | 2021-12-24 11:12:27 | 2021-12-24 11:14:16 | 2021-12-24 11:15:20 | bulb replaced | [8 empty] | FRC | Light fused-v.bala-low
FID4911 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 8 > Delivery Suite 5 |  | 2021-12-24 11:02:36 | 2021-12-27 11:48:08 | 2021-12-27 11:48:39 | 2021-12-28 09:06:01 | 2021-12-28 09:07:10 | 2021-12-28 09:07:51 | Adjusted the temperature make it warm | [8 empty] | FRC | Aircon make warm-Isyamudin-low
FID4910 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 1 > A&E Critical Care Counter |  | 2021-12-24 10:55:01 | 2021-12-24 10:56:34 | 2021-12-24 11:00:21 | 2021-12-24 11:00:58 | 2021-12-24 11:01:26 | 2021-12-24 11:01:56 | replaced new bulb | [8 empty] | FRC | Light fused-Senthil-low
FID4907 | Plumbing & Sanitary | WC / Squatting Pedestal | Damaged / Loose / Cracked | More than 1 room | RMG > RH > 7 > OT Male Channing Rm |  | 2021-12-24 10:07:56 | 2021-12-24 10:39:15 | 2021-12-24 10:39:39 | 2021-12-24 10:40:05 | 2021-12-24 10:42:06 | 2021-12-24 10:42:41 | Replace new set | [8 empty] | FRC | Toilet seat cover faulty-Nazri-low
FID4906 | Building | Door Bell | Unserviceable | More than 1 room | RMG > RH > 7 > CSSD |  | 2021-12-24 09:53:25 | 2021-12-24 10:00:51 | 2021-12-24 10:01:21 | 2021-12-24 10:04:04 | 2021-12-24 10:05:16 | 2021-12-24 10:06:13 | replaced battery | [8 empty] | FRC | Door bell not working-v.bala-low
FID4904 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 10 > Doctor's Lounge |  | 2021-12-24 09:27:41 | 2021-12-24 09:43:29 | 2021-12-24 09:43:58 | 2021-12-24 09:44:30 | 2021-12-24 09:45:24 | 2021-12-24 09:45:59 | done | [8 empty] | FRC | Light fused-nazri-low
FID4894 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 12 |  | 2021-12-24 00:57:21 | 2021-12-24 00:58:20 | 2021-12-24 00:58:50 | 2021-12-24 00:59:25 | 2021-12-24 01:00:21 | 2021-12-24 01:01:09 | adjusted the setpoint from bms from 28 to 22 |  |  |  |  | ray from ot |  |  |  | FRC | Aircon make cool-satha-low
FID4893 | Mechanical | BMS / BAS | Too hot / Too cold | Affecting Public | RMG > RH > 8 > Delivery Suite 3 |  | 2021-12-24 00:55:49 | 2021-12-24 01:01:49 | 2021-12-24 01:02:36 | 2021-12-24 01:03:26 | 2021-12-24 01:05:51 | 2021-12-24 01:07:00 | adjusted the temperature from 16 to 22 |  |  |  |  | staff from delivery ward |  |  |  | FRC | Aircon make warm-satha-low
FID4889 | Medical Equipment | Fridges & Freezers | Other: Fridge not cold | Affecting Public | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 7 |  | 2021-12-23 17:01:55 | 2021-12-27 11:19:10 | 2021-12-27 11:19:32 | 2021-12-27 11:20:30 | 2021-12-27 11:21:57 | 2021-12-28 13:51:57 | Fridge spoilt, not cold and can sense burning smell when open the fridge. Pending for follow-up |  |  |  |  | Siti |  |  |  | FRC | Fridge not cold-Isyamudin-low
FID4887 | Office and Furniture | Wall Clock | Cannot operate / defective | Affecting Public | RMG > RH > 9 > Ward 969 - 970 |  | 2021-12-23 17:00:07 | 2021-12-23 17:06:08 | 2021-12-23 17:06:58 | 2021-12-23 17:07:28 | 2021-12-23 17:11:07 | 2021-12-23 17:13:03 | Replaced new battery |  |  |  |  | Jasmine (HK) |  |  |  | FRC | Wall clock not working-mani-low
FID4886 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 13 > Ward 13 |  | 2021-12-23 16:45:40 | 2021-12-23 16:46:31 | 2021-12-23 16:46:57 | 2021-12-23 16:47:16 | 2021-12-23 16:47:38 | 2021-12-23 16:49:09 | Adjusted AHU 13-1 temperature setpoint from 20c to 16c in bms system make it cool. Cooling valve automatically increase from 0% to 17% | [8 empty] | FRC | Aircon make it cool-Su-low
FID4885 | Medical Equipment | Medical Gas | Change Cylinders | Affecting Public | RMG > RH > 2 > Dental Clinic |  | 2021-12-23 16:44:24 | 2021-12-23 17:20:19 | 2021-12-23 17:23:53 | 2021-12-23 17:24:16 | 2021-12-23 17:24:38 | 2021-12-23 17:26:07 | Checked onsite, the nitrous oxide cylinder is different from what we have. Need to order. Under follow-up |  |  |  |  | Angelina |  |  |  | FRC | Need 2x nitrous oxide cylinder-V.Bala-medium
FID4880 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 13 > Ward 1328-1336 |  | 2021-12-23 16:07:20 | 2021-12-23 16:07:45 | 2021-12-23 16:08:06 | 2021-12-23 16:08:28 | 2021-12-23 16:08:50 | 2021-12-23 16:18:39 | Adjusted VAV 1-2-9 setpoint from 24c to 21c and VAV 1-2-10 setpoint from 24c to 20c in bms system make it cool. | [8 empty] | FRC | Aircon make it cool-Su-low
FID4877 | Building | Filter | Choked | Affecting Public | RMG > RH > 7 > Operating Theatre 1 (Endoscopy) |  | 2021-12-23 14:56:06 | 2021-12-23 18:54:03 | 2021-12-23 18:54:25 | 2021-12-23 18:54:48 | 2021-12-23 18:55:09 | 2021-12-23 18:55:54 | Filter have Changed | [8 empty] | FRC | Need to replace new filter-Allan-low
FID4873 | Office and Furniture | Cabinet | Misaligned / dangling | Affecting Public | RMG > RSC > 16 > Eye Centre Consult Rm 7 |  | 2021-12-23 14:06:28 | 2021-12-27 11:13:37 | 2021-12-27 11:14:00 | 2021-12-27 11:14:24 | 2021-12-27 11:16:45 | 2021-12-27 11:17:14 | Tighten the cabinet door hinge | [8 empty] | FRC | Cabinet door hinge loose -nazri-low
FID4872 | Electrical | Light Bulb | Other: Light cannot turn off | Localised to room | RMG > RH > 9 > Ward 978 - 979 |  | 2021-12-23 14:04:03 | 2021-12-23 14:15:24 | 2021-12-23 14:22:40 | 2021-12-23 14:26:26 | 2021-12-23 14:27:01 | 2021-12-23 14:28:41 | off the light | [8 empty] | FRC | Bed head light cannot turn off-a.bala-low
FID4870 | Medical Equipment | Medical Gas | Alarm | Affecting Public | RMG > RH > 7 > Operating Theatre 6 |  | 2021-12-23 13:26:07 | 2021-12-27 11:08:07 | 2021-12-27 11:08:55 | 2021-12-27 11:09:24 | 2021-12-27 11:10:58 | 2021-12-27 11:12:03 | Checked and found the OLR tripped. Reset back to normal. Pump 1 currently running. | [8 empty] | FRC | AGSS pump not running-shanmu-high
FID4867 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 10 > Doctor's Lounge |  | 2021-12-23 12:37:44 | 2021-12-23 14:10:44 | 2021-12-23 14:11:12 | 2021-12-23 14:11:43 | 2021-12-23 14:12:16 | 2021-12-23 14:14:05 | replaced new light bulb | [8 empty] | FRC | Need to change bulb-A.Bala-low
FID4866 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 7 > Handicap Toilet 1 |  | 2021-12-23 12:22:00 | 2021-12-27 11:05:22 | 2021-12-27 11:05:49 | 2021-12-27 11:06:18 | 2021-12-27 11:06:43 | 2021-12-27 11:07:23 | Cleared the choke |  |  |  |  | Housekeeping |  |  |  | FRC | Basin choke-nazri-low
FID4865 | Office and Furniture | TV | Cannot operate / defective | Localised to room | RMG > RH > 9 > Ward 920 |  | 2021-12-23 12:20:45 | 2021-12-23 12:26:08 | 2021-12-23 12:26:39 | 2021-12-23 12:27:07 | 2021-12-23 12:28:03 | 2021-12-23 12:31:02 | Tv power wire loose and normal back |  |  |  |  | Housekeeping |  |  |  | FRC | TV not working-mani-low
FID4864 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 9 > Ward 950 |  | 2021-12-23 12:01:55 | 2021-12-23 12:08:30 | 2021-12-23 12:10:16 | 2021-12-23 12:12:13 | 2021-12-23 12:13:10 | 2021-12-23 12:15:55 | replaced new light bulb |  |  |  |  | Housekeeping |  |  |  | FRC | Light flickering-a.bala-low
FID4861 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-23 10:39:46 | 2021-12-23 11:46:14 | 2021-12-23 11:46:58 | 2021-12-23 11:47:32 | 2021-12-23 11:49:31 | 2021-12-23 11:50:44 | replaced co2 cylinder big 1 |  |  |  |  | Erick |  |  |  | FRC | Need 1 big CO2 cylinder-V.Bala-medium
FID4860 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 2 > Dental Surgery 10 |  | 2021-12-23 10:38:34 | 2021-12-27 10:50:08 | 2021-12-27 10:51:26 | 2021-12-27 10:51:47 | 2021-12-27 11:04:10 | 2021-12-27 11:04:39 | Replaced 2 big oxygen cylinder | [8 empty] | FRC | Need to replace 2 big oxygen cylinder-nazri-medium
FID4856 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > ESWL |  | 2021-12-23 09:57:24 | 2021-12-23 12:49:21 | 2021-12-23 12:49:41 | 2021-12-23 12:50:01 | 2021-12-23 12:50:22 | 2021-12-23 12:50:57 | Work done | [8 empty] | FRC | Need 1 big oxygen cylinder-Allan-medium
FID4852 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > Women Centre |  | 2021-12-23 09:43:45 | 2021-12-23 09:47:48 | 2021-12-23 09:49:12 | 2021-12-23 09:50:24 | 2021-12-23 09:51:11 | 2021-12-23 09:52:41 | replaced new light bulb |  |  |  |  | Housekeeping |  |  |  | FRC | Light flickering -a.bala-low
FID4851 | Office and Furniture | Patient Bed | Cannot operate / defective | Localised to room | RMG > RSC > 13 > Surgical Ctr |  | 2021-12-23 09:41:24 | 2021-12-23 09:42:08 | 2021-12-23 09:44:31 | 2021-12-23 09:45:18 | 2021-12-23 09:49:04 | 2021-12-23 09:51:24 | wire connection come out fixed back normal | [8 empty] | FRC | Bed cannot adjust-v.bala-low
FID4850 | Mechanical | AHU / FCU / CU | Noisy | Affecting Public | RMG > RSC > 13 > Visitor Lift Lobby |  | 2021-12-23 09:40:15 | 2021-12-27 10:46:55 | 2021-12-27 10:47:17 | 2021-12-27 10:47:38 | 2021-12-27 10:47:59 | 2021-12-27 10:49:23 | Noise coming from air purifier. Turned off the air purifier |  |  |  |  | Felix |  |  |  | FRC | Noise coming from the FCU-aru-low
FID4849 | Office and Furniture | Cabinet | Cannot open / close | Localised to room | RMG > RSC > 12 > Orthopaedic Ctr |  | 2021-12-23 09:37:29 | 2021-12-23 09:38:39 | 2021-12-23 09:39:09 | 2021-12-23 09:52:29 | 2021-12-23 09:53:23 | 2021-12-23 09:56:34 | staff locker cannot open informed security use master key open | [8 empty] | FRC | Staff locker cannot open-V.Bala-low
FID4848 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > RM@RH Counter |  | 2021-12-23 09:34:58 | 2021-12-23 09:39:39 | 2021-12-23 09:40:08 | 2021-12-23 09:42:10 | 2021-12-23 09:43:15 | 2021-12-23 09:44:34 | replaced new light bulb |  |  |  |  | Staff |  |  |  | FRC | No light-a.bala-low
FID4839 | Medical Equipment | Medical Gas | Alarm | More than 1 room | RMG > RH > 7M > Level 7M |  | 2021-12-23 08:36:14 | 2021-12-23 08:38:41 | 2021-12-23 08:39:08 | 2021-12-23 08:40:44 | 2021-12-23 08:43:12 | 2021-12-23 08:44:23 | pumb trip then rest back to normal | [8 empty] | FRC | AGSS pump not running-ilayaraja-high
FID4838 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Ward 920 |  | 2021-12-23 03:14:52 | 2021-12-23 03:16:08 | 2021-12-23 03:16:30 | 2021-12-23 03:16:50 | 2021-12-23 03:17:31 | 2021-12-23 03:18:09 | close diffuser for two rooms also | [8 empty] | FRC | 920,917 aircon make warm -satha-low
FID4837 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-23 01:30:43 | 2021-12-23 01:43:56 | 2021-12-23 01:44:53 | 2021-12-23 01:45:43 | 2021-12-23 01:46:13 | 2021-12-23 01:47:10 | adjusted setpoint temperature from bms | [8 empty] | FRC | Aircon make warm-satha-low
FID4831 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-22 17:25:18 | 2021-12-22 17:28:31 | 2021-12-22 17:28:51 | 2021-12-22 17:29:11 | 2021-12-22 17:29:32 | 2021-12-22 17:30:13 | Adjusted the temperature setpoint from 28c to 20c and damper position from 100% auto to 0% manual in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID4830 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2021-12-22 16:48:05 | 2021-12-22 22:05:48 | 2021-12-22 22:06:11 | 2021-12-22 22:06:34 | 2021-12-22 22:06:57 | 2021-12-22 22:07:30 | Work done | [8 empty] | FRC | Need to open patient locker -Allan-low
FID4827 | Mechanical | Lift & Escalators (Schindler) | Other: Lift door keep open and closeLift door keep open and close, for all levels | Whole Building | RMG > RH > All > Patient Lift 11 |  | 2021-12-22 15:46:21 | 2021-12-23 09:15:40 | 2021-12-23 09:16:05 | 2021-12-23 09:16:24 | 2021-12-23 09:16:44 | 2021-12-23 09:17:36 | schindler contractor check and lift normal back | [8 empty] | FRC | Lift door keep open and close, for all levels -mani-low
FID4825 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1059 |  | 2021-12-22 15:37:01 | 2021-12-22 15:42:04 | 2021-12-22 15:42:22 | 2021-12-22 15:42:40 | 2021-12-22 15:43:04 | 2021-12-22 15:47:48 | Adjusted vav 1-1-17 temperature setpoint from 20c to 24c in bms system make it warm. damper position automatically reduce from 90% open to 20%. | [8 empty] | FRC | Aircon too cold, make it warm-su-low
FID4824 | Building | Door Knob / Handle | Unable to open or close properly | Localised to room | RMG > RSC > 8 > Children Centre Consult Rm 3 |  | 2021-12-22 15:35:14 | 2021-12-22 22:08:22 | 2021-12-22 22:09:02 | 2021-12-22 22:09:23 | 2021-12-22 22:09:45 | 2021-12-22 22:10:42 | Need to change the lock now don’t have stock | [8 empty] | FRC | Door handle loose-Allan-low
FID4822 | Medical Equipment | Fridges & Freezers | Other: fridge got smell | Localised to room | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 7 |  | 2021-12-22 15:30:17 | 2021-12-22 17:16:51 | 2021-12-22 17:17:17 | 2021-12-22 17:18:36 | 2021-12-22 17:19:59 | 2021-12-22 17:21:09 | fridge smell clean retun back | [8 empty] | FRC | Fridge got smell-Aru-low
FID4816 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 2 > Passenger Lift Lobby |  | 2021-12-22 14:22:29 | 2021-12-23 09:18:37 | 2021-12-23 09:19:05 | 2021-12-23 09:19:29 | 2021-12-23 09:19:56 | 2021-12-23 09:21:00 | Replaced new bulb | [8 empty] | FRC | Light fused-mani-low
FID4815 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > Dental Clinic |  | 2021-12-22 14:21:43 | 2021-12-23 09:45:24 | 2021-12-23 09:46:00 | 2021-12-23 09:46:27 | 2021-12-23 09:46:54 | 2021-12-23 09:49:03 | Replaced new bulb |  |  |  |  | Abu (HK) |  |  |  | FRC | Signage light bulb fused-mani-low
FID4814 | Plumbing & Sanitary | Soap Dispenser | Other: Soap dispenser dropped | Localised to room | RMG > RH > 2 > Dental X-Ray |  | 2021-12-22 14:19:10 | 2021-12-23 10:45:16 | 2021-12-23 10:45:51 | 2021-12-23 10:46:39 | 2021-12-23 10:47:03 | 2021-12-23 10:48:18 | Fixed back the soap dispenser on the wall |  |  |  |  | Staff |  |  |  | FRC | Soap dispenser dropped-Hossain-low
FID4813 | Office and Furniture | Cabinet | Other: Screw loose | Localised to room | RMG > RH > 7 > CSSD |  | 2021-12-22 14:18:19 | 2021-12-22 14:53:12 | 2021-12-22 14:53:32 | 2021-12-22 14:53:52 | 2021-12-22 14:54:14 | 2021-12-22 14:54:47 | Yes done |  |  |  |  | John |  |  |  | FRC | Cabinet screw loose -allan-low
FID4811 | Building | Door Closer | Unable to open or close properly | Localised to room | RMG > RH > 8 > Delivery Suite 5 |  | 2021-12-22 13:30:33 | 2021-12-22 13:40:47 | 2021-12-22 13:41:08 | 2021-12-22 13:41:27 | 2021-12-22 13:41:47 | 2021-12-22 13:42:17 | Done already | [8 empty] | FRC | Door cannot stay open-allan-low
FID4809 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 817 |  | 2021-12-22 13:28:11 | 2021-12-23 10:51:56 | 2021-12-23 10:52:20 | 2021-12-23 10:52:47 | 2021-12-23 10:53:13 | 2021-12-23 10:54:05 | Adjusted the aircon temperature in bms system make it warm | [8 empty] | FRC | Aircon make it warm-isyamudin-low
FID4807 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 8 > Ward 855 |  | 2021-12-22 13:24:49 | 2021-12-23 10:55:03 | 2021-12-23 10:55:28 | 2021-12-23 10:55:52 | 2021-12-23 10:56:17 | 2021-12-23 10:56:50 | Replaced new wall clock battery |  |  |  |  | Sister Png |  |  |  | FRC | Wall clock not working-Hossain-low
FID4802 | Electrical | Vending Machine | Other: Out of order | Affecting Public | RMG > RSC > 13 > Surgical Ctr |  | 2021-12-22 10:51:55 | 2021-12-23 10:57:36 | 2021-12-23 10:58:00 | 2021-12-23 10:58:26 | 2021-12-23 10:58:50 | 2021-12-23 10:59:51 | Reset the machine power but still not working. Indicates failure list nozzle. Informed to Atlas vending vendor to check. Rectified |  |  |  |  | Staff |  |  |  | FRC | Coffee vending machine out of order-Hossain-low
FID4801 | Electrical | Vending Machine | Unserviceable | Localised to room | RMG > RH > 7 > Corridor |  | 2021-12-22 10:50:54 | 2021-12-22 11:07:13 | 2021-12-22 11:07:44 | 2021-12-22 11:08:34 | 2021-12-22 11:09:04 | 2021-12-22 11:14:15 | Remove the cutlery box normal back |  |  |  |  | Day Surgery Business Centre Staff |  |  |  | FRC | Chef-in-a-box vending machine cutlery stuck-mani-low
FID4800 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 7 > OT Clean Corridor |  | 2021-12-22 10:49:39 | 2021-12-22 11:22:09 | 2021-12-22 11:22:45 | 2021-12-22 11:24:37 | 2021-12-22 11:25:31 | 2021-12-22 11:37:43 | Replaced new bulb 2 nos |  |  |  |  | Staff |  |  |  | FRC | Light flickering -mani-low
FID4799 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2021-12-22 10:48:29 | 2021-12-22 11:18:16 | 2021-12-22 11:18:40 | 2021-12-22 11:19:02 | 2021-12-22 11:19:26 | 2021-12-22 11:20:06 | Done I have open |  |  |  |  | Staff |  |  |  | FRC | Patient locker need to open -allan-low
FID4797 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-22 10:35:24 | 2021-12-22 10:36:09 | 2021-12-22 10:36:34 | 2021-12-22 10:36:54 | 2021-12-22 10:37:13 | 2021-12-22 10:38:42 | delivered one Co2 cylinder | [8 empty] | FRC | Need one CO2 cylinder to be replaced- Shanmu-medium
FID4791 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1337-1343 |  | 2021-12-22 09:31:35 | 2021-12-22 09:32:04 | 2021-12-22 09:32:28 | 2021-12-22 09:32:54 | 2021-12-22 09:33:35 | 2021-12-22 10:03:42 | Adjusted ahu setpoint temperature. | [8 empty] | FRC | Aircon make it cool-su-low
FID4789 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 818 |  | 2021-12-22 09:07:51 | 2021-12-23 11:01:00 | 2021-12-23 11:01:25 | 2021-12-23 11:01:50 | 2021-12-23 11:02:16 | 2021-12-23 11:02:55 | Adjusted the temperature setpoint in bms system make it cool | [8 empty] | FRC | Aircon very warm, make it cool-isyamudin-low
FID4778 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 8 > Delivery Suite 6 |  | 2021-12-22 08:44:54 | 2021-12-22 08:51:40 | 2021-12-22 08:52:24 | 2021-12-22 08:53:01 | 2021-12-22 08:53:48 | 2021-12-22 09:08:45 | replaced new light bulb | [8 empty] | FRC | Light fused-a.bala-low
FID4777 | Building | Door Frame | Misaligned / dangling | More than 1 room | RMG > RH > 9 > Business Centre Office 2 |  | 2021-12-22 08:40:56 | 2021-12-22 08:43:13 | 2021-12-22 08:43:38 | 2021-12-22 08:44:06 | 2021-12-22 08:44:57 | 2021-12-22 08:45:52 | door closer screw adjusted | [8 empty] | FRC | Door hinge loose-v.bala-low
FID4776 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 2 > Dental Clinic |  | 2021-12-22 08:37:51 | 2021-12-23 11:04:53 | 2021-12-23 11:05:18 | 2021-12-23 11:05:44 | 2021-12-23 11:06:10 | 2021-12-23 11:06:39 | Replaced new light | [8 empty] | FRC | Light fused -senthil-low
FID4775 | Plumbing & Sanitary | Urinal | Choked | More than 1 room | RMG > RSC > 2 > Male Toilet |  | 2021-12-22 08:28:39 | 2021-12-22 22:13:16 | 2021-12-22 22:13:44 | 2021-12-22 22:14:05 | 2021-12-22 22:14:27 | 2021-12-22 22:15:27 | Work done | [8 empty] | FRC | Urinal choke-Allan-low
FID4772 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 8 > Ward 854 |  | 2021-12-22 01:13:52 | 2021-12-22 01:14:31 | 2021-12-22 01:15:09 | 2021-12-22 01:15:31 | 2021-12-22 01:15:46 | 2021-12-22 01:17:47 | adjusted the aircon temprature make it cold | [8 empty] | FRC | Aircon make it cold-a.bala-low
FID4771 | Mechanical | AHU / FCU / CU | Misaligned / dangling | More than 1 room | RMG > RH > 10 > Stn D Corridor |  | 2021-12-22 00:36:43 | 2021-12-22 00:38:27 | 2021-12-22 00:38:58 | 2021-12-22 00:39:20 | 2021-12-22 00:39:52 | 2021-12-22 00:40:28 | fixed back | [8 empty] | FRC | Diffuser dropped-v.bala-low
FID4770 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 9 > Corridor |  | 2021-12-21 22:24:35 | 2021-12-21 22:29:03 | 2021-12-21 22:29:56 | 2021-12-21 22:30:25 | 2021-12-21 22:30:49 | 2021-12-21 22:32:02 | replaced new light bulb | [8 empty] | FRC | Light fused -a.bala-low
FID4769 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-21 19:36:28 | 2021-12-23 11:07:26 | 2021-12-23 11:07:50 | 2021-12-23 11:08:16 | 2021-12-23 11:08:41 | 2021-12-23 11:09:14 | Replaced 1 big CO2 cylinder |  |  |  |  | ray from ot |  |  |  | FRC | Need one big co2 cylinder-nazri-medium
FID4768 | Plumbing & Sanitary | Water Heater | Damaged / Loose / Cracked | Localised to room | RMG > RH > 7 > OT Tea Rm |  | 2021-12-21 19:33:50 | 2021-12-21 19:37:41 | 2021-12-21 19:45:06 | 2021-12-21 19:45:51 | 2021-12-21 19:46:47 | 2021-12-21 19:47:45 | replace new tap no more leaking |  |  |  |  | STAFF FROM OT |  |  |  | FRC | Water dispenser hot water leaking-satha-low
FID4765 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 12 > Rehab Con Rm 3 |  | 2021-12-21 16:52:05 | 2021-12-23 11:10:10 | 2021-12-23 11:10:35 | 2021-12-23 11:11:01 | 2021-12-23 11:11:32 | 2021-12-23 11:12:59 | Adjusted VAV 12-1-5 temperature setpoint from 24c to 21c and damper position set to 65% manually in bms system make it cool | [8 empty] | FRC | Aircon make it cool-ilayaraja-low
FID4763 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 818 |  | 2021-12-21 16:48:55 | 2021-12-21 16:54:32 | 2021-12-21 16:55:10 | 2021-12-21 17:02:23 | 2021-12-21 17:05:28 | 2021-12-21 17:06:59 | adjusted the thermostat not working . close diffuser for 70 percent . | [8 empty] | FRC | Aircon make it cool-aru-low
FID4762 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-21 16:47:57 | 2021-12-21 17:02:23 | 2021-12-21 17:02:53 | 2021-12-21 17:04:43 | 2021-12-21 17:13:59 | 2021-12-21 17:15:22 | replaced the new cylinder |  |  |  |  | Erick |  |  |  | FRC | Need to replace 1 big CO2 cylinder-ilayaraja-medium
FID4761 | Medical Equipment | Fridges & Freezers | Other: Fridge not cold | Localised to room | RMG > RH > 8 > Nursing Stn B |  | 2021-12-21 16:43:23 | 2021-12-21 16:56:07 | 2021-12-21 16:56:33 | 2021-12-21 16:56:58 | 2021-12-21 16:57:55 | 2021-12-21 16:59:19 | replace battery | [8 empty] | FRC | Medication fridge showing low and not cold-satha-low
FID4760 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 12 > Rehab Con Rm 2 |  | 2021-12-21 16:38:14 | 2021-12-21 16:45:16 | 2021-12-21 16:45:46 | 2021-12-21 16:46:10 | 2021-12-21 16:46:32 | 2021-12-21 17:28:40 | Adjusted vav 12-1-6 temperature setpoint from 21c to 19c and damper position from auto (38%) to 60% manual in bms system make it cool | [8 empty] | FRC | Aircon make it cool-su-low
FID4759 | Building | Door Stopper | Other: Door unable to stay open | Localised to room | RMG > RSC > 12 > Rehab Con Rm 2 |  | 2021-12-21 16:36:52 | 2021-12-23 11:14:16 | 2021-12-23 11:14:41 | 2021-12-23 11:15:53 | 2021-12-23 11:16:25 | 2021-12-23 11:16:56 | Repaired the door | [8 empty] | FRC | Door unable to stay open -ming cai-low
FID4758 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 1 > A&E |  | 2021-12-21 16:35:48 | 2021-12-23 11:17:51 | 2021-12-23 11:18:16 | 2021-12-23 11:18:49 | 2021-12-23 11:19:14 | 2021-12-23 11:20:13 | Adjusted FCU 1-10-1 temperature setpoint from 23c to 21c and cooling valve from 50% to 55% in bms system make it cool |  |  |  |  | Kelvin |  |  |  | FRC | Aircon make it cool-isyamudin-low
FID4757 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 6 |  | 2021-12-21 16:05:55 | 2021-12-21 16:06:21 | 2021-12-21 16:06:39 | 2021-12-21 16:06:57 | 2021-12-21 16:07:16 | 2021-12-21 16:09:55 | Adjusted the temperature setpoint from 16c to 14c and heater to 0% manual in bms system make it cooler |  |  |  |  | ray |  |  |  | FRC | Aircon make it cool-su-low
FID4755 | Electrical | Light Bulb | Other: Different colour | Affecting Public | RMG > RH > All > Passenger Lift 6 |  | 2021-12-21 15:49:27 | 2021-12-23 10:32:53 | 2021-12-23 10:33:17 | 2021-12-23 10:33:56 | 2021-12-23 10:34:21 | 2021-12-23 10:36:55 | Replaced to 840 light tube |  |  |  |  | Wee Khim |  |  |  | FRC | Need to replace the light in VL6, different colour -senthil-low
FID4754 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Affecting Public | RMG > RH > 9 > Ward 960 - 961 |  | 2021-12-21 15:42:56 | 2021-12-21 16:04:29 | 2021-12-21 16:05:37 | 2021-12-21 16:06:14 | 2021-12-21 16:14:46 | 2021-12-21 16:20:22 | replaced the new hose & spray |  |  |  |  | Staff |  |  |  | FRC | Bidet spray faulty-ilayaraja-low
FID4753 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 1 > A&E |  | 2021-12-21 15:41:57 | 2021-12-21 15:43:28 | 2021-12-21 15:43:48 | 2021-12-21 15:44:07 | 2021-12-21 15:44:27 | 2021-12-21 15:50:19 | Adjusted FCU 1-10-1 cooling valve from 40% to 50% in bms system make it cool. Temperature setpoint is 23c |  |  |  |  | Kelvin |  |  |  | FRC | Aircon make it cool-su-low
FID4752 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 9 > Corridor |  | 2021-12-21 15:10:21 | 2021-12-21 15:31:38 | 2021-12-21 15:31:58 | 2021-12-21 15:32:22 | 2021-12-21 15:32:43 | 2021-12-21 15:33:16 | Bulb change done | [8 empty] | Su | Light fused-allan-low
FID4750 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-21 14:45:14 | 2021-12-21 14:49:10 | 2021-12-21 14:49:30 | 2021-12-21 14:49:51 | 2021-12-21 15:04:05 | 2021-12-21 15:11:29 | Adjusted the temperature setpoint from 28c to 20c and heater from auto (100%) to 0% manual in bms system make it cool | [8 empty] | Su | Aircon make it cool-su-low
FID4749 | Medical Equipment | Fridges & Freezers | Other: Fridge not cold | Localised to room | RMG > RH > 8 > Nursing Stn B |  | 2021-12-21 14:43:13 | 2021-12-21 14:43:57 | 2021-12-21 14:44:28 | 2021-12-21 14:44:52 | 2021-12-21 14:46:00 | 2021-12-21 14:52:00 | clear the ice reduce the setpoint checked compressor running normal | [8 empty] | Su | Medication fridge showing low and not cold-satha-low
FID4744 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-21 13:55:38 | 2021-12-23 11:21:03 | 2021-12-23 11:21:29 | 2021-12-23 11:21:55 | 2021-12-23 11:23:15 | 2021-12-23 11:24:41 | Checked onsite, there is airflow, but not so cold. So adjusted AHU 9-2 temperature setpoint from 20c to 18c in bms system make it cool |  |  |  |  | Staff |  |  |  | FRC | Aircon make it cool-isyamudin-low
FID4743 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 1 > Nuclear Med Office |  | 2021-12-21 13:54:47 | 2021-12-21 13:56:33 | 2021-12-21 13:56:53 | 2021-12-21 13:57:13 | 2021-12-21 13:57:33 | 2021-12-21 13:59:43 | Adjusted AHU 1-5 temperature setpoint from 22.5c to 22c in bms system make it cool. Cooling valve increased from 63% to 73%. |  |  |  |  | Staff |  |  |  | FRC | Aircon make it cool-su-low
FID4739 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 13 > Ward 1337-1343 Nurse Station |  | 2021-12-21 13:08:04 | 2021-12-21 13:26:37 | 2021-12-21 13:26:57 | 2021-12-21 13:27:18 | 2021-12-21 13:27:40 | 2021-12-21 13:28:16 | Change battery |  |  |  |  | Staff |  |  |  | FRC | Need to replace wall clock battery-allan-low
FID4738 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 13 > Ward 1328-1336 Nurse Station |  | 2021-12-21 13:06:59 | 2021-12-21 13:29:13 | 2021-12-21 13:29:40 | 2021-12-21 13:30:04 | 2021-12-21 13:30:29 | 2021-12-21 13:31:17 | Change battery done |  |  |  |  | Staff |  |  |  | FRC | Need to replace wall clock battery-allan-low
FID4736 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > RIPC Waiting Area |  | 2021-12-21 12:23:52 | 2021-12-23 11:25:35 | 2021-12-23 11:26:02 | 2021-12-23 11:27:17 | 2021-12-23 11:27:43 | 2021-12-23 11:28:11 | Replaced new light |  |  |  |  | abu hk |  |  |  | FRC | Need to change the ceiling light-Nazri-low
FID4732 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 1 > Level 1 |  | 2021-12-21 11:32:47 | 2021-12-21 11:39:21 | 2021-12-21 11:42:35 | 2021-12-21 11:43:17 | 2021-12-21 11:43:39 | 2021-12-21 11:45:24 | Delivered 5 nos O2 cylinders to facilities |  |  |  |  | Yu How |  |  |  | FRC | Need to send 5 takeo oxygen cylinders for CC-shanmu-low
FID4731 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 8 > Ward 812 |  | 2021-12-21 11:25:27 | 2021-12-23 11:29:08 | 2021-12-23 11:29:33 | 2021-12-23 11:29:58 | 2021-12-23 11:30:22 | 2021-12-23 11:31:25 | Replaced new wall clock battery |  |  |  |  | Housekeeping |  |  |  | FRC | Need to replace new wall clock battery-nazri-low
FID4727 | Plumbing & Sanitary | Urinal | Choked | Affecting Public | RMG > RSC > 2 > Male Toilet |  | 2021-12-21 09:55:28 | 2021-12-21 11:28:30 | 2021-12-21 11:29:02 | 2021-12-21 11:30:01 | 2021-12-21 11:30:56 | 2021-12-21 11:32:01 | cleared the chock |  |  |  |  | Naing (HK) |  |  |  | FRC | Urinal choke-ilayaraja-low
FID4717 | Office and Furniture | Patient Bed | Cannot operate / defective | Localised to room | RMG > RH > 9 > Ward 973 - 975 |  | 2021-12-21 09:27:12 | 2021-12-21 11:36:28 | 2021-12-21 11:37:03 | 2021-12-21 11:37:39 | 2021-12-21 11:39:24 | 2021-12-21 11:40:55 | reset the power then back to normal | [8 empty] | FRC | Bed not working-ilayaraja-low
FID4708 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-21 08:57:28 | 2021-12-21 09:16:59 | 2021-12-21 09:17:35 | 2021-12-21 09:18:07 | 2021-12-21 09:20:56 | 2021-12-21 09:26:58 | adjusted temperature in 23 degree | [8 empty] | FRC | Aircon too cold, make it warm-V.bala-low
FID4707 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 13 > Ward 1328-1336 Nurse Station |  | 2021-12-21 08:26:49 | 2021-12-21 10:06:45 | 2021-12-21 10:07:18 | 2021-12-21 10:08:08 | 2021-12-21 10:08:47 | 2021-12-21 10:09:42 | battery chain | [8 empty] | FRC | Need to replace wall clock battery-alan-low
FID4706 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn C |  | 2021-12-21 08:06:54 | 2021-12-21 08:15:18 | 2021-12-21 08:15:47 | 2021-12-21 08:16:18 | 2021-12-21 08:18:20 | 2021-12-21 08:22:10 | adjusted vav control in bms setpoint 24to22 make it cool | [8 empty] | FRC | Aircon too warm-v.bala-low
FID4705 | Office and Furniture | Telephone | Cannot operate / defective | Localised to room | RMG > RH > 9 > Ward 919 |  | 2021-12-21 08:02:43 | 2021-12-23 11:32:39 | 2021-12-23 11:33:03 | 2021-12-23 11:34:16 | 2021-12-23 11:34:41 | 2021-12-23 11:35:17 | Adjusted the telephone connection | [8 empty] | FRC | Telephone not working-v.bala-low
FID4704 | Electrical | Light Bulb | Tripped / Short-Circuit / Overloaded | Localised to room | RMG > RH > 7 > Day Surgery Corridor |  | 2021-12-21 07:58:58 | 2021-12-21 08:53:26 | 2021-12-21 08:55:01 | 2021-12-21 09:21:08 | 2021-12-21 09:21:49 | 2021-12-21 09:23:02 | replaced new light bulb | [8 empty] | FRC | Lights trip-abala-high
FID4703 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 9 > Ward 978 - 979 |  | 2021-12-21 07:51:33 | 2021-12-21 08:46:48 | 2021-12-21 08:47:24 | 2021-12-21 08:47:52 | 2021-12-21 08:48:28 | 2021-12-21 08:49:22 | replaced new light bulb | [8 empty] | FRC | Call bell keep ringing-abala-low
FID4702 | Building | Filter | Dirty / Odour | Localised to room | RMG > RH > 7 > CSSD |  | 2021-12-21 07:37:12 | 2021-12-21 07:38:04 | 2021-12-21 07:38:27 | 2021-12-21 07:38:48 | 2021-12-21 07:39:35 | 2021-12-21 07:40:10 | replaced new filter | [8 empty] | FRC | Need to change new filter-v.bala-low
FID4701 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-21 00:42:36 | 2021-12-21 00:43:49 | 2021-12-21 00:44:20 | 2021-12-21 00:44:44 | 2021-12-21 00:46:56 | 2021-12-21 00:47:40 | adjusted vav control in bms setpoint 20to24 make it warm | [8 empty] | FRC | Aircon too cold, make it warm-v.bala-low
FID4699 | Mechanical | BMS / BAS | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-20 18:51:10 | 2021-12-20 18:52:34 | 2021-12-20 18:52:57 | 2021-12-20 18:53:26 | 2021-12-20 18:53:52 | 2021-12-20 18:55:49 | temprature setpoint at 26 degree heater manully 0 % change to auto 100 % |  |  |  |  | Staff |  |  |  | FRC | Aircon make it warm to 24, aircon too cool-satha-low
FID4698 | Mechanical | AHU / FCU / CU | Leaking / Condensation | Affecting Public | RMG > RSC > 1 > Visitor Lift Lobby |  | 2021-12-20 18:42:36 | 2021-12-20 18:43:05 | 2021-12-20 18:43:27 | 2021-12-20 18:43:51 | 2021-12-20 18:45:24 | 2021-12-20 18:46:13 | vaccume drain pipe and clear the choke |  |  |  |  | Staff from screening area |  |  |  | FRC | Water leaking from the ceiling aircon-satha-low
FID4695 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 12 > Raffles Health Screeners |  | 2021-12-20 17:57:02 | 2021-12-20 18:14:55 | 2021-12-20 18:15:23 | 2021-12-20 18:15:44 | 2021-12-20 18:16:10 | 2021-12-20 18:16:36 | clear |  |  |  |  | Valar |  |  |  | FRC | Basin choke-ming cai-low
FID4694 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-20 17:48:00 | 2021-12-20 17:48:44 | 2021-12-20 17:49:11 | 2021-12-20 17:49:39 | 2021-12-20 17:50:23 | 2021-12-20 17:57:32 | adjusted setpoint to 22 degree in bms |  |  |  |  | staff from 10 D |  |  |  | FRC | Aircon make it cool-satha-low
FID4692 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 11 > MRO |  | 2021-12-20 16:58:31 | 2021-12-21 13:33:45 | 2021-12-21 13:34:07 | 2021-12-21 13:34:29 | 2021-12-21 13:35:05 | 2021-12-21 13:35:44 | Bulb change done | [8 empty] | FRC | Need to change the ceiling light-Allan-low
FID4689 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 8 > Delivery Suite 3 |  | 2021-12-20 15:58:56 | 2021-12-20 16:01:50 | 2021-12-20 16:02:53 | 2021-12-20 16:05:25 | 2021-12-20 16:05:44 | 2021-12-20 16:06:21 | Adjust setpoint temperature. | [8 empty] | FRC | Aircon need to make cool-Isyamudin-low
FID4688 | Mechanical | Mechanical Ventilation | Cannot Open or Close | More than 1 room | RMG > RH > 9 > Ward 973 - 975 |  | 2021-12-20 15:28:17 | 2021-12-23 11:37:51 | 2021-12-23 11:38:39 | 2021-12-23 11:39:03 | 2021-12-23 11:39:40 | 2021-12-23 11:40:10 | Repaired the bed | [8 empty] | FRC | Bed cannot adjust up and down -ming cai-low
FID4686 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 7 > Histo Data Rm |  | 2021-12-20 15:04:05 | 2021-12-21 13:36:44 | 2021-12-21 13:37:05 | 2021-12-21 13:37:28 | 2021-12-21 13:37:56 | 2021-12-21 13:38:26 | Bulb change done | [8 empty] | FRC | Need to replace the ceiling light-Allan-low
FID4685 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1065 |  | 2021-12-20 14:58:51 | 2021-12-20 15:06:51 | 2021-12-20 15:07:28 | 2021-12-20 15:10:44 | 2021-12-20 15:13:23 | 2021-12-20 15:15:43 | adjested the setpoint & airflow from bms | [8 empty] | FRC | Aircon very cool, make it warm - ilayaraja-low
FID4680 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 7 > Day Surgery Rm 13 |  | 2021-12-20 12:49:38 | 2021-12-20 14:29:33 | 2021-12-20 14:29:52 | 2021-12-20 14:30:12 | 2021-12-20 14:30:53 | 2021-12-20 14:32:12 | clear the chock |  |  |  |  | Abu (HK) |  |  |  | FRC | Basin choke -ming cai-low
FID4677 | Office and Furniture | Cabinet | Cannot open / close | Affecting Public | RMG > RH > 2 > Dental Surgery 3 |  | 2021-12-20 11:45:39 | 2021-12-20 16:57:27 | 2021-12-20 16:57:51 | 2021-12-20 16:58:10 | 2021-12-20 16:58:39 | 2021-12-20 16:59:15 | open the door | [8 empty] | FRC | Drawer stuck-ming cai-low
FID4675 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 1 > Nuclear Medicine Centre |  | 2021-12-20 11:44:28 | 2021-12-20 11:57:21 | 2021-12-20 11:58:16 | 2021-12-20 12:03:03 | 2021-12-20 12:04:43 | 2021-12-20 12:06:23 | replaced the new oxigen cylinder | [8 empty] | FRC | Need to change 1 small oxygen cylinder for e-trolley-ilayaraja-medium
FID4671 | Plumbing & Sanitary | Soap Dispenser | Other: Relocation | Localised to room | RMG > RH > 1 > Unit #01-11 Retail Phamacy |  | 2021-12-20 11:01:00 | 2021-12-20 11:12:31 | 2021-12-20 11:12:52 | 2021-12-20 11:13:16 | 2021-12-20 11:28:45 | 2021-12-20 11:30:28 | Move to the opposite side | [8 empty] | FRC | Need to relocate hand towel dispenser -ming cai-low
FID4670 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1052 |  | 2021-12-20 10:53:58 | 2021-12-20 11:43:13 | 2021-12-20 11:43:42 | 2021-12-20 11:44:46 | 2021-12-20 11:45:37 | 2021-12-20 11:47:24 | adjusted the setpoint temperature to 24 degrees and position at 20 % opening .checked on site |  |  |  |  | Staff |  |  |  | FRC | Aircon make it warm -satha-low
FID4668 | Mechanical | Fire Extinguisher | Misaligned / dangling | Localised to room | RMG > RH > 11 > Bed Lift Lobby |  | 2021-12-20 10:20:48 | 2021-12-20 11:49:47 | 2021-12-20 11:50:27 | 2021-12-20 11:50:34 | 2021-12-20 11:50:40 | 2021-12-20 11:53:32 | fixed back |  |  |  |  | Senthil |  |  |  | FRC | Fire extinguisher dropped-Shanmu-low
FID4667 | Mechanical | Autodoor | Misaligned / dangling | Localised to room | RMG > RSC > 11 > Fireman Lift Lobby |  | 2021-12-20 10:18:44 | 2021-12-20 10:25:04 | 2021-12-20 10:50:32 | 2021-12-20 10:52:58 | 2021-12-20 12:53:23 | 2021-12-23 11:36:35 | Tighten the door & lock screw back to normal |  |  |  |  | Mohan (FCC) |  |  |  | FRC | Need to check alignment of the EM door, EM lock not touching-ilayaraja-low
FID4666 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | Localised to room | RMG > RH > 12 > RHS Male Toilet |  | 2021-12-20 10:14:42 | 2021-12-20 10:25:52 | 2021-12-20 10:47:22 | 2021-12-20 10:47:52 | 2021-12-20 10:48:17 | 2021-12-20 10:48:46 | Cleared the choke |  |  |  |  | Naing (HK) |  |  |  | FRC | Toilet bowl choke-Allan-low
FID4665 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 11 > MRO |  | 2021-12-20 10:12:33 | 2021-12-23 10:29:25 | 2021-12-23 10:30:00 | 2021-12-23 10:30:35 | 2021-12-23 10:31:34 | 2021-12-23 10:32:05 | Replaced new light | [8 empty] | FRC | Light fused-Senthil-low
FID4664 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 11 > Room 1115 (CTU) |  | 2021-12-20 10:11:37 | 2021-12-23 10:26:01 | 2021-12-23 10:26:26 | 2021-12-23 10:26:51 | 2021-12-23 10:27:17 | 2021-12-23 10:27:52 | Replaced new light |  |  |  |  | Pei Yu |  |  |  | FRC | Light fused-Senthil-low
FID4660 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RSC > 9 > Internal Med |  | 2021-12-20 09:22:34 | 2021-12-20 11:50:27 | 2021-12-20 11:50:49 | 2021-12-20 11:51:28 | 2021-12-20 11:51:58 | 2021-12-20 11:54:51 | ddc failed restart back normal | [8 empty] | FRC | Aircon very warm -satha-low
FID4652 | Mechanical | Lift & Escalators | System Shows fault / Error code | Localised to room | RMG > RSC > B1 > B1 |  | 2021-12-20 08:46:35 | 2021-12-20 08:52:38 | 2021-12-20 08:53:24 | 2021-12-20 08:53:49 | 2021-12-20 08:54:28 | 2021-12-20 08:57:52 | Reset normal back | [8 empty] | FRC | Escalator 05 not running, error code '4' -mani-low
FID4651 | Medical Equipment | Mortuary Fridge & Freezers | Alarm | Localised to room | RMG > RSC > 11 > Radiology |  | 2021-12-20 08:42:02 | 2021-12-20 10:44:37 | 2021-12-20 10:45:01 | 2021-12-20 10:45:26 | 2021-12-20 10:46:05 | 2021-12-20 10:46:36 | Replaced new battery for testo data logger | [8 empty] | FRC | Testo data logger not working -aru-low
FID4649 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-20 08:33:07 | 2021-12-20 10:41:28 | 2021-12-20 10:41:54 | 2021-12-20 10:42:18 | 2021-12-20 10:43:02 | 2021-12-20 10:43:38 | Adjusted the aircon temperature in bms system make it cool | [8 empty] | FRC | Aircon make it cool -aru-low
FID4648 | Office and Furniture | TV | Cannot open / close | Localised to room | RMG > RH > 7 > Call Centre |  | 2021-12-20 08:12:39 | 2021-12-20 08:12:59 | 2021-12-20 08:13:19 | 2021-12-20 08:13:44 | 2021-12-20 08:14:05 | 2021-12-20 08:17:09 | Replaced new battery | [8 empty] | FRC | TV remote not working -mani -low
FID4647 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 1 > A&E |  | 2021-12-20 08:07:31 | 2021-12-20 10:38:26 | 2021-12-20 10:38:51 | 2021-12-20 10:39:14 | 2021-12-20 10:40:17 | 2021-12-20 10:40:55 | Replaced new oxygen cylinder | [8 empty] | FRC | Need to replace 2 big oxygen cylinder -aru-medium
FID4645 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > A&E Waiting Area |  | 2021-12-20 07:38:27 | 2021-12-20 07:38:49 | 2021-12-20 07:39:32 | 2021-12-20 07:39:57 | 2021-12-20 07:40:26 | 2021-12-20 07:44:23 | Replaced new bulb | [8 empty] | FRC | Need to change bulb -mani-low
FID4644 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 1 > A&E Bed 1 & 2 |  | 2021-12-20 07:30:18 | 2021-12-20 07:30:51 | 2021-12-20 07:31:22 | 2021-12-20 07:31:58 | 2021-12-20 07:32:17 | 2021-12-20 07:35:24 | call bell Reset normal back | [8 empty] | FRC | Call bell not ringing-mani-low
FID4639 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1065 |  | 2021-12-19 18:29:02 | 2021-12-19 18:30:10 | 2021-12-19 18:30:54 | 2021-12-19 18:32:05 | 2021-12-19 18:34:08 | 2021-12-19 18:36:09 | Bms adjuted the aircon temprature make it warm | [8 empty] | FRC | Aircon make it warm-a.bala-low
FID4637 | Plumbing & Sanitary | Basin / sink | Choked | More than 1 room | RMG > RH > 10 > Ward 1061 |  | 2021-12-19 18:13:36 | 2021-12-19 18:20:59 | 2021-12-19 18:22:49 | 2021-12-19 18:23:18 | 2021-12-19 18:24:29 | 2021-12-19 18:25:49 | basin choke cleared | [8 empty] | FRC | Basin choke-v.bala-low
FID4635 | Mechanical | Pneumatic Tube | System Shows fault / Error code | More than 1 room | RMG > RH > 2 > RM@RH Counter |  | 2021-12-19 17:03:06 | 2021-12-19 17:04:11 | 2021-12-19 17:04:38 | 2021-12-19 17:05:02 | 2021-12-19 17:05:26 | 2021-12-19 17:07:52 | working normal test to send tube and recived back | [8 empty] | FRC | Pneumatic tube system not working-satha-low
FID4633 | Office and Furniture | Chair | Cannot operate / defective | More than 1 room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-19 16:38:37 | 2021-12-19 17:33:31 | 2021-12-19 17:34:00 | 2021-12-19 17:34:42 | 2021-12-19 17:35:52 | 2021-12-19 17:38:32 | screw missing replaced new screw | [8 empty] | FRC | Need to tighten screw-v.bala-low
FID4632 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Nursing Stn C |  | 2021-12-19 16:15:01 | 2021-12-19 16:42:13 | 2021-12-19 16:42:39 | 2021-12-19 16:43:21 | 2021-12-19 17:39:37 | 2021-12-19 17:43:34 | adjusted vav control in bms aircon make it cool | [8 empty] | FRC | Aircon make it cool-v.bala-low
FID4631 | Building | Door Frame | Noisy | More than 1 room | RMG > RH > 8 > Ward 850 |  | 2021-12-19 14:30:40 | 2021-12-19 16:05:17 | 2021-12-19 16:05:45 | 2021-12-19 16:06:10 | 2021-12-19 16:08:26 | 2021-12-19 16:10:00 | door closer screw loose tighten back normal | [8 empty] | FRC | Door very noisy-v.bala-low
FID4627 | Office and Furniture | Safe Box | Cannot open / close | More than 1 room | RMG > RH > 13 > Ward 1328-1336 |  | 2021-12-19 11:57:43 | 2021-12-19 13:41:53 | 2021-12-19 13:42:44 | 2021-12-19 13:43:10 | 2021-12-19 13:43:42 | 2021-12-19 13:44:37 | number locker cannot open master key use | [8 empty] | FRC | Patient locker need to open-v.bala-low
FID4625 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 13 |  | 2021-12-19 09:41:36 | 2021-12-20 10:50:43 | 2021-12-20 10:51:06 | 2021-12-20 10:51:32 | 2021-12-20 10:51:55 | 2021-12-20 10:52:39 | Manually adjust the cooling valve onsite to make the aircon warm | [8 empty] | FRC | Aircon too cold, make it warm-isyamudin-low
FID4620 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 13 |  | 2021-12-19 03:41:44 | 2021-12-19 04:01:14 | 2021-12-19 04:01:43 | 2021-12-19 04:03:29 | 2021-12-19 04:05:06 | 2021-12-19 04:06:33 | setpoint adjust 24to 26 aircon make it warm | [8 empty] | FRC | Aircon make it warm-aru-low
FID4619 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1328-1336 |  | 2021-12-19 03:29:28 | 2021-12-19 03:30:06 | 2021-12-19 03:30:34 | 2021-12-19 03:31:31 | 2021-12-19 03:31:57 | 2021-12-19 03:37:29 | adjusted the aircon temperature from 20c to 25c and damber from auto to 20% manual in bms system make it warm | [8 empty] | FRC | Aircon make it warm-mani-low
FID4617 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | Localised to room | RMG > RH > 13 > Ward 1310-1318, RMG |  | 2021-12-18 22:37:52 | 2021-12-18 22:39:49 | 2021-12-18 22:40:16 | 2021-12-18 22:42:20 | 2021-12-18 22:44:01 | 2021-12-18 22:45:37 | room setpoint adjust 24 to 26 aircon make it warm | [8 empty] | FRC | Aircon make it warm -aru-low
FID4616 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > A&E |  | 2021-12-18 21:59:05 | 2021-12-18 21:59:31 | 2021-12-18 22:00:04 | 2021-12-18 22:00:35 | 2021-12-18 22:04:55 | 2021-12-18 22:07:18 | Replaced new bulb | [8 empty] | FRC | Light fused-mani-low
FID4615 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1009 |  | 2021-12-18 21:19:28 | 2021-12-20 10:35:05 | 2021-12-20 10:35:29 | 2021-12-20 10:35:54 | 2021-12-20 10:36:19 | 2021-12-20 10:37:30 | Reduce the room vav damper position in bms system to make it warm | [8 empty] | FRC | Aircon make it warm -aru-low
FID4612 | Office and Furniture | Safe Box | Cannot open / close | More than 1 room | RMG > RH > 13 > Ward 1328-1336 Nurse Station |  | 2021-12-18 20:20:30 | 2021-12-18 20:32:21 | 2021-12-18 20:32:49 | 2021-12-18 20:33:16 | 2021-12-18 20:35:17 | 2021-12-18 20:36:40 | cabinet number locker cannot open master key use open | [8 empty] | FRC | Patient locker cannot lock-v.bala-low
FID4611 | Plumbing & Sanitary | Basin / sink | Choked | More than 1 room | RMG > RH > 12 > Housekeeping Office |  | 2021-12-18 20:01:11 | 2021-12-18 20:37:23 | 2021-12-18 20:37:48 | 2021-12-18 20:38:11 | 2021-12-18 20:38:49 | 2021-12-18 20:39:26 | choke clear | [8 empty] | FRC | Basin choke-v.bala-low
FID4608 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1328-1336 |  | 2021-12-18 18:24:19 | 2021-12-18 18:25:01 | 2021-12-18 18:25:33 | 2021-12-18 18:26:03 | 2021-12-18 18:29:38 | 2021-12-18 19:04:29 | adjusted vav control in bms make it warm | [8 empty] | FRC | Aircon too cold, make it warm-v.bala-low
FID4606 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1351-1357 |  | 2021-12-18 17:12:16 | 2021-12-18 17:31:45 | 2021-12-18 17:32:12 | 2021-12-18 17:34:52 | 2021-12-18 17:37:06 | 2021-12-18 17:38:09 | adjusted vav control in bms make it cool | [8 empty] | FRC | Aircon too cold, make it warm-v.bala-low
FID4603 | Office and Furniture | TV | Cannot operate / defective | More than 1 room | RMG > RH > 10 > Ward 1007 |  | 2021-12-18 14:27:49 | 2021-12-18 14:48:17 | 2021-12-18 14:48:41 | 2021-12-18 14:49:11 | 2021-12-18 14:49:33 | 2021-12-18 14:50:27 | Power failure reset back to normal | [8 empty] | FRC | TV not working-Senthil-low
FID4601 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1337-1343 |  | 2021-12-18 13:59:45 | 2021-12-18 14:00:15 | 2021-12-18 14:00:40 | 2021-12-18 14:00:51 | 2021-12-18 14:02:24 | 2021-12-18 14:03:37 | adjusted the temprature aircon make it warm | [8 empty] | FRC | Aircon make it warm-a.bala-low
FID4600 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Nursing Stn C |  | 2021-12-18 13:35:55 | 2021-12-18 14:45:49 | 2021-12-18 14:46:29 | 2021-12-18 14:50:26 | 2021-12-18 14:51:25 | 2021-12-18 14:52:15 | air | [8 empty] | FRC | Aircon stuffy-nazri-low
FID4598 | Mechanical | AHU / FCU / CU | Other: Room pressure low | Localised to room | RMG > RH > 9 > Ward 954 (BMT) |  | 2021-12-18 12:02:12 | 2021-12-20 10:31:49 | 2021-12-20 10:32:14 | 2021-12-20 10:32:38 | 2021-12-20 10:33:02 | 2021-12-20 10:33:47 | Adjusted the temperature setpoint on the isolation room display panel from 21c to 19c |  |  |  |  | Staff |  |  |  | FRC | Room pressure low-nazri-low
FID4597 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-18 12:00:42 | 2021-12-18 12:33:40 | 2021-12-18 12:34:01 | 2021-12-18 12:34:29 | 2021-12-18 12:34:50 | 2021-12-18 12:38:31 | Adjusted the aircon temperature make it warm | [8 empty] | FRC | Aircon make it cool-satha-low
FID4595 | Mechanical | AHU / FCU / CU | Unserviceable | Localised to room | RMG > RH > 7 > Angio Suite |  | 2021-12-18 11:51:03 | 2021-12-20 10:28:08 | 2021-12-20 10:28:48 | 2021-12-20 10:29:16 | 2021-12-20 10:29:40 | 2021-12-20 10:30:18 | Replaced new AAA battery for hygrometer |  |  |  |  | Sogie |  |  |  | FRC | Hygrometer no battery-Allan-low
FID4594 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1011 |  | 2021-12-18 11:49:11 | 2021-12-18 12:41:12 | 2021-12-18 12:42:52 | 2021-12-18 12:45:44 | 2021-12-18 12:56:57 | 2021-12-18 12:57:34 | Adjusted the room vav temperature setpoint and damper position in bms system |  |  |  |  | Staff |  |  |  | FRC | Aircon make it warm-ilayaraja-low
FID4593 | Office and Furniture | Wall Clock | Cannot operate / defective | Localised to room | RMG > RH > 13 > Ward 1345-1350 |  | 2021-12-18 11:48:22 | 2021-12-18 15:16:41 | 2021-12-18 15:17:07 | 2021-12-18 15:17:40 | 2021-12-18 15:18:06 | 2021-12-18 15:18:53 | Change Battery |  |  |  |  | Staff |  |  |  | FRC | Wall clock not working-Allan-low
FID4592 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 13 > Ward 1351-1357 |  | 2021-12-18 11:47:15 | 2021-12-18 12:23:05 | 2021-12-18 12:30:40 | 2021-12-18 12:31:04 | 2021-12-18 12:31:38 | 2021-12-18 12:32:42 | Adjusted the room vav temperature setpoint in bms system make it warm |  |  |  |  | Staff |  |  |  | FRC | Aircon make it warm-satha-low
FID4591 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1345-1350 |  | 2021-12-18 11:45:15 | 2021-12-18 12:07:21 | 2021-12-18 12:13:42 | 2021-12-18 12:19:12 | 2021-12-18 12:21:07 | 2021-12-18 12:22:16 | Adjusted the aircon temperature for the room vav in bms system make it warm |  |  |  |  | Staff |  |  |  | FRC | Aircon make it warm-satha-low
FID4590 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 8 > Ward 851 |  | 2021-12-18 11:27:46 | 2021-12-18 11:38:46 | 2021-12-18 11:39:38 | 2021-12-18 11:41:26 | 2021-12-18 11:42:43 | 2021-12-18 11:44:10 | replaced new light bulb | [8 empty] | Arasan Balasubramanian | Mirror light fused-nazri-low
FID4589 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > RM@RH Counter |  | 2021-12-18 11:23:53 | 2021-12-18 11:36:19 | 2021-12-18 11:37:22 | 2021-12-18 11:49:41 | 2021-12-18 11:50:14 | 2021-12-18 11:51:39 | replaced new light bulb | [8 empty] | Arasan Balasubramanian | Light bulb fused -a.bala-low
FID4587 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 852 |  | 2021-12-18 10:30:14 | 2021-12-18 10:38:11 | 2021-12-18 11:07:19 | 2021-12-18 11:08:08 | 2021-12-18 11:08:38 | 2021-12-18 11:09:41 | adjusted the cool8ng valve | [8 empty] | Muhammad Nazri Bin Mohamad | Aircon too warm-nazri-low
FID4582 | Mechanical | Air Diffuser (supply/return) | Airflow too strong / weak | Localised to room | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-18 07:30:17 | 2021-12-18 07:31:16 | 2021-12-18 07:33:16 | 2021-12-18 07:34:15 | 2021-12-18 07:42:00 | 2021-12-18 07:43:29 | close the valve to 50 % from 100 % |  |  |  |  | STAFF FROM OT |  |  |  | FRC | satha , low
FID4581 | Medical Equipment | Autoclave | Leaking | Localised to room | RMG > RH > 7 > CSSD |  | 2021-12-18 07:17:02 | 2021-12-18 07:18:56 | 2021-12-18 07:19:47 | 2021-12-18 07:38:10 | 2021-12-18 07:40:53 | 2021-12-18 07:44:45 | cssd Autoclave 3 water leaking from hose need to arrange the contrectar for replace the hose | [8 empty] | Muthu Sathasivam | ilayaraja, medium
FID4580 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | More than 1 room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-18 03:12:13 | 2021-12-18 03:14:07 | 2021-12-18 03:14:34 | 2021-12-18 03:15:01 | 2021-12-18 03:19:56 | 2021-12-18 03:21:41 | checked setting on BMS motor running in 45 Hz reduce to 30 Hz and setpoint increased from 16 degree to 19 degree . checked on site back to normal |  |  |  |  | staff from STN 9B |  |  |  | FRC | satha , low
FID4578 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1319-1327 |  | 2021-12-17 22:44:10 | 2021-12-17 22:45:54 | 2021-12-17 22:46:25 | 2021-12-17 22:46:51 | 2021-12-17 22:55:36 | 2021-12-17 22:57:47 | change to manual mode running normally . DDC no signal to run . need to inform Honeywell. |  |  |  |  | staff from ward 13 |  |  |  | FRC | satha , low
FID4572 | Office and Furniture | Table | Misaligned / dangling | Localised to room | RMG > RH > 7 > Operating Theatre 10 |  | 2021-12-17 17:52:10 | 2021-12-18 10:48:14 | 2021-12-18 10:48:34 | 2021-12-18 10:48:56 | 2021-12-18 10:49:58 | 2021-12-18 10:51:30 | Fixed back the wheel | [8 empty] | Su | Hand table wheel come out-nazri-low
FID4570 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 12 |  | 2021-12-17 17:33:08 | 2021-12-18 09:43:13 | 2021-12-18 09:43:35 | 2021-12-18 09:43:58 | 2021-12-18 09:45:50 | 2021-12-18 09:46:36 | Adjusted the aircon temperature from 23c to 18c and damper from auto to 0% manual in bms system make it cool |  |  |  |  | Staff |  |  |  | FRC | Aircon make it cool-Su-low
FID4569 | Plumbing & Sanitary | Basin / sink | No water | Affecting Public | RMG > RH > 7 > OR9&10 Scrub Rm |  | 2021-12-17 17:31:01 | 2021-12-18 10:43:55 | 2021-12-18 10:44:17 | 2021-12-18 10:44:41 | 2021-12-18 10:45:03 | 2021-12-18 10:47:23 | Checked on site, water coming out but, low pressure. Adjusted the valve, basin water back to normal |  |  |  |  | Staff |  |  |  | FRC | Scrub sink no water-nazri-low
FID4568 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Localised to room | RMG > RH > 9 > Ward 917 |  | 2021-12-17 17:29:55 | 2021-12-18 10:21:47 | 2021-12-18 10:24:21 | 2021-12-18 10:24:52 | 2021-12-18 10:25:18 | 2021-12-18 10:25:58 | replaced new bidet spray | [8 empty] | FRC | Bidet spray leaking -nazri-low
FID4566 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 12 |  | 2021-12-17 16:06:04 | 2021-12-17 16:06:28 | 2021-12-17 16:06:47 | 2021-12-17 16:07:07 | 2021-12-17 16:07:55 | 2021-12-17 16:09:48 | Adjusted the temperature setpoint from 23c to 18c in bms system make it cool. Heater automatically reduced from 65% to 14%. |  |  |  |  | Doctor |  |  |  | FRC | Aircon make it cool-su-low
FID4565 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > Concierge |  | 2021-12-17 15:31:26 | 2021-12-17 15:42:02 | 2021-12-17 15:42:32 | 2021-12-17 15:42:56 | 2021-12-17 15:44:28 | 2021-12-17 15:48:24 | Replaced new bulb 2 nos |  |  |  |  | Omar |  |  |  | FRC | Light fused -mani-low
FID4564 | Electrical | Light Bulb | Misaligned / dangling | Localised to room | RMG > RH > 2 > Raffles Chinese Medicine Clinic |  | 2021-12-17 14:59:12 | 2021-12-17 15:00:46 | 2021-12-17 15:01:13 | 2021-12-17 15:01:55 | 2021-12-17 15:02:27 | 2021-12-17 15:06:56 | Replaced new screw |  |  |  |  | Sherry |  |  |  | FRC | Light fitting screw loose-mani-low
FID4563 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 13 |  | 2021-12-17 14:24:54 | 2021-12-17 14:34:26 | 2021-12-17 14:34:50 | 2021-12-17 14:35:11 | 2021-12-17 14:35:31 | 2021-12-17 14:40:04 | Check on site ,Ahu 13-1 was on manual.,put back to auto mode..actuator upon checking not responding,.highlight to honeywell to follow up | [8 empty] | Su | Aircon too cold whole ward, make it warm-Isyamudin-low
FID4562 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-17 14:20:17 | 2021-12-17 15:28:24 | 2021-12-17 15:28:45 | 2021-12-17 15:36:01 | 2021-12-17 15:37:06 | 2021-12-17 15:38:08 | vav tamber manually open | [8 empty] | Su | Aircon make it cool -Aru-low
FID4561 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1048 |  | 2021-12-17 14:18:52 | 2021-12-17 14:20:55 | 2021-12-17 14:21:23 | 2021-12-17 14:21:43 | 2021-12-17 14:22:00 | 2021-12-17 14:23:07 | Adjusted the vav 1-1-28 temperature setpoint from 24c to 22c and damper position from 5% manual to auto (56.3%) in bms system make it cool. | [8 empty] | Su | Aircon make it cool -Su-low
FID4559 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 2 > Skin & Aesthetics Consult Rm 6 |  | 2021-12-17 14:04:30 | 2021-12-17 14:05:10 | 2021-12-17 14:05:28 | 2021-12-17 14:06:43 | 2021-12-17 14:07:01 | 2021-12-17 14:09:07 | Adjusted vav 5-1-7 temperature setpoint from 22c to 24c and damper position from 50% manual to 30% in bms system make it warm. |  |  |  |  | Siti |  |  |  | FRC | Aircon too cold, make it warm-Su-low
FID4558 | Plumbing & Sanitary | Urinal | Choked | Localised to room | RMG > RSC > 2 > Male Toilet |  | 2021-12-17 14:03:12 | 2021-12-18 11:07:19 | 2021-12-18 11:07:39 | 2021-12-18 11:07:59 | 2021-12-18 11:08:30 | 2021-12-18 11:08:59 | Cleared the urinal choke |  |  |  |  | Housekeeping |  |  |  | FRC | Urinal bowl choke-v.bala-low
FID4557 | Building | Window | Unable to open or close properly | Localised to room | RMG > RH > 12 > RHS Female Toilet |  | 2021-12-17 14:01:21 | 2021-12-17 14:58:58 | 2021-12-17 15:41:09 | 2021-12-17 17:22:47 | 2021-12-17 17:23:10 | 2021-12-17 17:24:56 | Put down the curtains |  |  |  |  | Suvin |  |  |  | FRC | Window blind faulty - ming cai-low
FID4553 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU Rm 708 |  | 2021-12-17 12:39:20 | 2021-12-17 13:07:09 | 2021-12-17 13:07:35 | 2021-12-17 13:08:44 | 2021-12-17 13:58:05 | 2021-12-17 13:58:43 | Manually close the room vav damper | [8 empty] | Rajendran Manikandan | aircon to cold ,make it warm -aru-low
FID4552 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RSC > 8 > ENT |  | 2021-12-17 11:40:01 | 2021-12-18 11:14:39 | 2021-12-18 11:15:01 | 2021-12-18 11:15:23 | 2021-12-18 11:16:13 | 2021-12-18 11:17:30 | Need to purchase bulb. Will follow-up |  |  |  |  | Jurice |  |  |  | FRC | Light fused-mani-low
FID4551 | Mechanical | Autodoor | Cannot Open or Close | Localised to room | RMG > RSC > 13 > Link Bridge |  | 2021-12-17 11:05:06 | 2021-12-18 11:18:48 | 2021-12-18 11:19:10 | 2021-12-18 11:19:32 | 2021-12-18 11:19:54 | 2021-12-18 11:21:28 | Unable to rectify the door issue. Engaged entre contractor to check. Work done |  |  |  |  | Suvin |  |  |  | FRC | Door slam very loud and EM lock not touching-a.bala-low
FID4550 | Mechanical | Autodoor | Other: EM lock not touching | Localised to room | RMG > RSC > 19 > Level 19 |  | 2021-12-17 11:03:39 | 2021-12-18 10:57:56 | 2021-12-18 10:58:17 | 2021-12-18 10:58:37 | 2021-12-18 10:59:02 | 2021-12-18 11:03:38 | Adjusted the EM door alignment, EM lock working back to normal. |  |  |  |  | Naing (HK) |  |  |  | FRC | Need to check alignment of the EM door, EM lock not touching-v.bala-low
FID4549 | Office and Furniture | Cabinet | Cannot open / close | Localised to room | RMG > RH > 11 > Room 1107 (QM) |  | 2021-12-17 11:00:31 | 2021-12-17 11:02:04 | 2021-12-17 11:38:49 | 2021-12-17 11:39:20 | 2021-12-17 11:40:02 | 2021-12-17 13:08:25 | Change a new cabinet |  |  |  |  | Shafie |  |  |  | FRC | Top-hanging cabinet cannot lock-ming cai-low
FID4546 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2021-12-17 10:34:26 | 2021-12-18 09:49:33 | 2021-12-18 09:49:54 | 2021-12-18 09:50:16 | 2021-12-18 09:50:41 | 2021-12-18 10:09:10 | Replaced new cylinders |  |  |  |  | Staff |  |  |  | FRC | Need to replace 2 big CO2 cylinder-nazri-medium
FID4545 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-17 10:32:28 | 2021-12-17 10:44:13 | 2021-12-17 10:44:33 | 2021-12-17 10:44:59 | 2021-12-17 10:45:23 | 2021-12-17 10:48:48 | Adjusted the temperature setpoint from 25c to 18c and heater from 100% manual to auto (0%) in bms system make it cool. |  |  |  |  | Staff |  |  |  | FRC | Aircon make it cool -Su-low
FID4544 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1358-1363 |  | 2021-12-17 10:30:46 | 2021-12-17 10:35:54 | 2021-12-17 10:38:17 | 2021-12-17 10:38:37 | 2021-12-17 10:38:55 | 2021-12-17 10:43:44 | Adjusted the vav number 1-2-15 damper position from 20% to 5% and vav 1-2-16 temperature setpoint from 24c to 26c and damper from 20% to 5% in bms system make it warm |  |  |  |  | Staff |  |  |  | FRC | Aircon make it warm -su-low
FID4543 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 12 > REMC Counter |  | 2021-12-17 10:29:09 | 2021-12-17 11:05:17 | 2021-12-17 11:09:48 | 2021-12-17 11:10:32 | 2021-12-17 11:10:58 | 2021-12-17 11:12:57 | aircon make it cool colling valve adjust 40 to 60 |  |  |  |  | Staff |  |  |  | FRC | Aircon make it cool -Aru-low
FID4542 | Building | Door Lock | Unable to open or close properly | Localised to room | RMG > RSC > 11 > Radiology |  | 2021-12-17 10:23:48 | 2021-12-17 12:49:36 | 2021-12-17 12:49:53 | 2021-12-17 13:02:55 | 2021-12-17 13:03:15 | 2021-12-17 15:05:49 | open the lock | [8 empty] | FRC | Door lock faulty -ming cai-low
FID4539 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 7 > ICU Rm 705 |  | 2021-12-17 10:17:24 | 2021-12-17 10:37:38 | 2021-12-17 10:39:37 | 2021-12-17 10:40:35 | 2021-12-17 10:41:32 | 2021-12-17 10:44:26 | call bell rreset back to normal |  |  |  |  | Staff |  |  |  | FRC | Call bell not ringing-a.bala-low
FID4537 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 16 > Eye Centre Consult Rm 1 |  | 2021-12-17 10:15:50 | 2021-12-17 11:06:59 | 2021-12-17 11:07:25 | 2021-12-17 11:08:43 | 2021-12-17 11:09:06 | 2021-12-17 11:12:29 | Adjusted VAV 16-2-4 temperature setpoint to 24c and damper position to 20% manual in bms system | [8 empty] | FRC | Aircon make it warm-ilayaraja-low
FID4536 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > RHS Male Toilet |  | 2021-12-17 10:09:51 | 2021-12-17 10:49:39 | 2021-12-17 10:51:35 | 2021-12-17 10:52:47 | 2021-12-17 10:53:39 | 2021-12-17 10:54:31 | replaced new light bulb |  |  |  |  | Staff |  |  |  | FRC | Ceiling light fused-a.bala-low
FID4535 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2021-12-17 10:06:57 | 2021-12-17 10:12:23 | 2021-12-17 11:52:21 | 2021-12-17 11:53:18 | 2021-12-17 11:56:28 | 2021-12-17 14:12:39 | Cabinet drawer number lock cannot open. Used master key to open the cabinet drawer |  |  |  |  | Staff |  |  |  | FRC | Need to open patient safe drawer-v.bala-low
FID4533 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 7 |  | 2021-12-17 09:47:03 | 2021-12-17 10:12:04 | 2021-12-17 10:12:33 | 2021-12-17 10:13:01 | 2021-12-17 10:13:28 | 2021-12-17 10:24:13 | then just put 'Suspect dimmer switch problem. When dim light, light flickering. |  |  |  |  | Siti |  |  |  | FRC | Light flickering -mani-low
FID4529 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 8 |  | 2021-12-17 07:22:13 | 2021-12-17 07:26:17 | 2021-12-17 07:26:47 | 2021-12-17 07:39:55 | 2021-12-17 07:40:23 | 2021-12-17 07:42:04 | adjusted setpoint fot OT 8 from 18 to 25 degree and active heater |  |  |  |  | STAFF FROM OT |  |  |  | FRC | Aircon make it warm to 24c for paeds case-ilayaraja-low
FID4528 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 9 > Nursing Stn B |  | 2021-12-17 07:18:42 | 2021-12-17 07:19:32 | 2021-12-17 07:22:51 | 2021-12-17 07:23:26 | 2021-12-17 07:25:19 | 2021-12-17 07:27:40 | checked on BMS setpoint on 15 degree so increase setpoint to 16 degree |  |  |  |  | staff from STN 9B |  |  |  | FRC | Aircon make warm, very cool in all place -satha-low
FID4527 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1319-1327 Nurse Station |  | 2021-12-17 01:35:07 | 2021-12-17 01:36:41 | 2021-12-17 01:37:28 | 2021-12-17 01:38:08 | 2021-12-17 01:39:18 | 2021-12-17 01:41:27 | setpoint temperature is in auto 24 degrees and vav opening position only 20 % . but still patient need to warm so adjusted VAV position to 10 %. | [8 empty] | FRC | Aircon make it warm -satha-low
FID4523 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1011 |  | 2021-12-16 18:47:27 | 2021-12-16 18:48:01 | 2021-12-16 18:48:42 | 2021-12-16 18:49:11 | 2021-12-16 18:49:37 | 2021-12-16 18:55:19 | adjusted the temperature setpoint form 24c to 30c and heater form auto to 100% manual in bms system | [8 empty] | FRC | Aircon make it warm -mani-low
FID4518 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 852 |  | 2021-12-16 16:09:08 | 2021-12-16 16:28:39 | 2021-12-16 17:08:02 | 2021-12-16 17:08:23 | 2021-12-16 17:08:44 | 2021-12-16 17:10:50 | Check on-site ahu 8-1 actuator jam..highlighted honeywell to follow up. |  |  |  |  | Cho |  |  |  | FRC | Aircon make it cool-isyamudin-low
FID4513 | Plumbing & Sanitary | Soap Dispenser | Other: FIx new | Localised to room | RMG > RH > 8 > Labour Ward Counter |  | 2021-12-16 14:58:35 | 2021-12-16 15:05:24 | 2021-12-16 15:06:24 | 2021-12-16 15:07:48 | 2021-12-16 15:09:06 | 2021-12-16 15:10:03 | work completed | [8 empty] | FRC | Need to remove old hand rub dispenser and install new one -v.bala-low
FID4512 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 10 > Heart Ctr Con Rm 5 |  | 2021-12-16 14:57:11 | 2021-12-16 15:02:03 | 2021-12-16 15:02:23 | 2021-12-16 15:02:43 | 2021-12-16 15:03:07 | 2021-12-16 15:03:54 | Adjusted VAV 10-1-17 temperature setpoint at 18c and damper from 85% manual to 95% manual in bms system make it cool slightly. |  |  |  |  | Dr Lee |  |  |  | FRC | Aircon make it slightly cool-su-low
FID4511 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 10 |  | 2021-12-16 14:56:18 | 2021-12-16 14:59:16 | 2021-12-16 14:59:53 | 2021-12-16 15:00:27 | 2021-12-16 15:00:51 | 2021-12-16 15:01:31 | Adjusted the temperature setpoint from 23c to 26c and heater from auto to 100% manual in bms system |  |  |  |  | Staff |  |  |  | FRC | Aircon make it warm-su-low
FID4506 | Plumbing & Sanitary | Tap | Leaking | Localised to room | RMG > RH > 7 > Clinical Lab |  | 2021-12-16 13:36:31 | 2021-12-16 13:47:26 | 2021-12-16 13:47:50 | 2021-12-16 13:48:14 | 2021-12-16 14:38:29 | 2021-12-16 17:45:29 | Need to purchase new tap. Awaiting for parts. |  |  |  |  | Felix |  |  |  | FRC | Basin tap leaking-v.bala-low
FID4505 | Electrical | Call System | Other: Keep ringing | Affecting Public | RMG > RH > 7 > OT |  | 2021-12-16 13:35:17 | 2021-12-16 13:36:00 | 2021-12-16 13:48:23 | 2021-12-16 13:48:44 | 2021-12-16 13:49:08 | 2021-12-16 15:11:42 | replaced spare faceplate |  |  |  |  | Sister cherry |  |  |  | FRC | Call bell keep ringing non-stop-mani-low
FID4504 | Plumbing & Sanitary | Basin / sink | Leaking | Affecting Public | RMG > RH > 9 > Nursing Stn D |  | 2021-12-16 13:33:40 | 2021-12-16 13:35:18 | 2021-12-16 13:38:05 | 2021-12-16 14:40:41 | 2021-12-16 14:41:46 | 2021-12-16 15:14:01 | onside checked no leaking | [8 empty] | FRC | Water leaking from basin-v.bala-low
FID4503 | Electrical | Call System | Other: Keep ringing | Localised to room | RMG > RH > 7 > Day Surgery |  | 2021-12-16 13:31:33 | 2021-12-16 13:36:05 | 2021-12-16 13:50:12 | 2021-12-16 13:51:10 | 2021-12-16 13:51:59 | 2021-12-16 14:02:18 | reset back to normal | [8 empty] | FRC | Call bell keep ringing non stop-a.bala-low
FID4502 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 11 > Admin Office Corridor |  | 2021-12-16 13:16:01 | 2021-12-16 16:06:21 | 2021-12-16 16:06:43 | 2021-12-16 16:07:05 | 2021-12-16 16:07:46 | 2021-12-16 16:08:22 | checked on site after adjust bms. ok |  |  |  |  | Jia Jing |  |  |  | FRC | Aircon too cold-aru-low
FID4500 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 7 > Molecular Lab PCR Rm |  | 2021-12-16 12:07:48 | 2021-12-16 12:10:42 | 2021-12-16 12:11:13 | 2021-12-16 12:11:38 | 2021-12-16 12:12:14 | 2021-12-16 12:17:02 | Replaced new bulb 5 nos |  |  |  |  | VJ |  |  |  | FRC | Need to replace fused bulb-mani-low
FID4499 | Building | Wall | Other: Photo frame | Localised to room | RMG > RH > 8 > Labour Ward Nursery |  | 2021-12-16 11:03:38 | 2021-12-16 15:18:08 | 2021-12-16 15:19:50 | 2021-12-16 15:23:47 | 2021-12-16 16:22:02 | 2021-12-16 16:22:26 | [5 empty] | Staff |  |  |  | FRC | Photo frame dropped-isyamudin-low
FID4496 | Plumbing & Sanitary | WC / Squatting Pedestal | Water flowing non-stop | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2021-12-16 10:44:16 | 2021-12-16 13:43:48 | 2021-12-16 13:44:11 | 2021-12-16 13:44:47 | 2021-12-16 13:45:10 | 2021-12-16 13:45:47 | flushing head screw adjusted and settled |  |  |  |  | Staff |  |  |  | FRC | Toilet flush not working-v.bala-low
FID4494 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2021-12-16 10:42:57 | 2021-12-16 11:16:59 | 2021-12-16 11:17:49 | 2021-12-16 11:18:12 | 2021-12-16 11:18:37 | 2021-12-16 11:21:06 | Check station D temperature ok.cant find anyone give the feedback |  |  |  |  | Staff |  |  |  | FRC | Aircon make it warm-a.bala.low
FID4493 | Plumbing & Sanitary | WC / Squatting Pedestal | Water flowing non-stop | Localised to room | RMG > RH > 13 > Ward 1358-1363 Nurse Station |  | 2021-12-16 10:40:39 | 2021-12-16 13:40:12 | 2021-12-16 13:40:36 | 2021-12-16 13:40:58 | 2021-12-16 13:41:38 | 2021-12-16 13:42:34 | settled non stop flushing complaint |  |  |  |  | Staff |  |  |  | FRC | Toilet flushing non-stop-aru-low
FID4492 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > Skin & Aesthetics Consult Rm 6 |  | 2021-12-16 10:36:53 | 2021-12-16 11:07:24 | 2021-12-16 11:07:49 | 2021-12-16 11:25:30 | 2021-12-16 11:25:53 | 2021-12-16 11:26:47 | Adjusted vav 5-1-7 temperature setpoint from 20c to 22c and damper from auto to 50% manual in bms system make it warm |  |  |  |  | Siti / Dr Chris Foo |  |  |  | FRC | Aircon too cold, make it warm-Su-low
FID4488 | Building Security System | CCTV System | Disconnected | Localised to room | RMG > RH > 11 > Bed Lift Lobby |  | 2021-12-16 10:28:26 | 2021-12-16 10:31:15 | 2021-12-16 10:45:18 | 2021-12-16 10:45:45 | 2021-12-16 10:46:10 | 2021-12-16 11:00:18 | Power Reset normal back | [8 empty] | Rajendran Manikandan | cctv camera not working mani -low
FID4486 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 1 (Endoscopy) |  | 2021-12-16 09:55:59 | 2021-12-16 10:04:53 | 2021-12-16 10:05:42 | 2021-12-16 10:06:43 | 2021-12-16 10:07:40 | 2021-12-16 10:08:28 | Adjusted the temperature setpoint and heater to 0% manual in bms system |  |  |  |  | Staff |  |  |  | FRC | Aircon make it cool, now showing 24c-Su-low
FID4485 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 11 |  | 2021-12-16 09:54:53 | 2021-12-16 10:00:25 | 2021-12-16 10:00:52 | 2021-12-16 10:01:17 | 2021-12-16 10:02:19 | 2021-12-16 10:03:04 | Adjusted the temperature setpoint from 22c to 18c and heater from 100% manual to 0% manual in bms system |  |  |  |  | Staff |  |  |  | FRC | Aircon make it cool to 18c, now showing 21c-Su-low
FID4484 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > Nuclear Medicine Centre |  | 2021-12-16 09:52:11 | 2021-12-16 10:05:06 | 2021-12-16 10:10:31 | 2021-12-16 10:10:55 | 2021-12-16 10:11:34 | 2021-12-16 10:12:10 | replace new bulb |  |  |  |  | Staff | 1 |  |  | FRC | Toilet light fused-a.bala-low
FID4483 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 2 |  | 2021-12-16 09:50:21 | 2021-12-16 09:56:55 | 2021-12-16 09:57:20 | 2021-12-16 09:57:43 | 2021-12-16 09:58:08 | 2021-12-16 09:59:09 | Adjusted VAV 5-1-5 temperature setpoint from 22c to 20c and damper position from 21.2% (auto) to 70% manual in bms system |  |  |  |  | Staff |  |  |  | FRC | No aircon -Su-low
FID4482 | Medical Equipment | Medical Gas | Other: medical gas O2 terminal leaking | Localised to room | RMG > RH > 8 > Ward 850 |  | 2021-12-16 09:31:26 | 2021-12-16 09:31:59 | 2021-12-16 09:32:20 | 2021-12-16 09:32:38 | 2021-12-16 09:32:42 | 2021-12-16 11:09:11 | ACA contractor replaced new oxygen terminal and o-rings |  | 2021-12-16 09:33:37 |  |  | staff form 8D |  |  |  | FRC | medical gas O2 terminal leaking-Shanmu-medium
FID4477 | Mechanical | BMS / BAS | Noisy | More than 1 room | RMG > RH > 10 > Ward 1060 |  | 2021-12-16 00:36:22 | 2021-12-16 00:40:18 | 2021-12-16 10:24:03 | 2021-12-16 10:24:26 | 2021-12-16 10:24:49 | 2021-12-16 10:26:06 | Adjusted room vav temperature setpoint in bms system make it cool | [8 empty] | FRC | Room aircon stuffy-v.bala-low
FID4476 | Office and Furniture | Wall Clock | Misaligned / dangling | Localised to room | RMG > RH > 8 > Ward 851 |  | 2021-12-15 21:57:39 | 2021-12-15 21:58:46 | 2021-12-16 10:21:50 | 2021-12-16 10:22:32 | 2021-12-16 10:22:54 | 2021-12-16 10:23:24 | Removed the wall clock as per request | [8 empty] | FRC | Request to remove wall clock-v.bala-low
FID4474 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | Localised to room | RMG > RH > 7 > OT Female Changing Rm |  | 2021-12-15 20:04:04 | 2021-12-15 20:06:48 | 2021-12-15 20:07:25 | 2021-12-15 20:07:54 | 2021-12-15 20:08:49 | 2021-12-15 20:20:38 | bowl choke unable to clear |  |  |  |  | wendy from house keeping |  |  |  | FRC | Toilet bowl choke-ilayaraja-medium
FID4472 | Building | Door Stopper | Unable to open or close properly | Localised to room | RMG > RH > 10 > Ward 1063 |  | 2021-12-15 18:14:38 | 2021-12-15 18:21:35 | 2021-12-15 18:30:33 | 2021-12-15 18:34:17 | 2021-12-15 18:34:56 | 2021-12-15 18:36:06 | screw loose tighten back to normal . |  |  |  |  | staff from 10 D |  |  |  | FRC | Need to fix door stopper-ilayaraja-low
FID4470 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > Women Centre |  | 2021-12-15 18:08:41 | 2021-12-15 18:09:24 | 2021-12-15 18:20:52 | 2021-12-15 18:24:49 | 2021-12-15 18:25:19 | 2021-12-15 18:26:03 | replaced new bulb 840/36W with starter. |  |  |  |  | yee hui |  |  |  | FRC | Light flickering-Senthil-low
FID4466 | Plumbing & Sanitary | Shower Fittings | Leaking | Localised to room | RMG > RH > 10 > Ward 1007 |  | 2021-12-15 15:33:54 | 2021-12-15 15:55:26 | 2021-12-15 15:55:55 | 2021-12-15 15:56:25 | 2021-12-15 15:56:52 | 2021-12-15 15:59:13 | Close the valve | [8 empty] | Su | Shower head water leaking-Ming cai-low
FID4464 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 11 > Office Pantry |  | 2021-12-15 14:42:13 | 2021-12-15 14:42:45 | 2021-12-15 15:07:38 | 2021-12-15 15:08:05 | 2021-12-15 15:09:14 | 2021-12-15 15:13:49 | Replaced new bulb | [8 empty] | Su | Need to change light bulb-mani-low
FID4463 | Mechanical | AHU / FCU / CU | Tripped / Short-Circuit / Overloaded | More than 1 room | RMG > RH > 11 > Facilities Dept. |  | 2021-12-15 14:32:27 | 2021-12-15 14:32:52 | 2021-12-15 14:33:13 | 2021-12-15 14:33:31 | 2021-12-15 14:33:54 | 2021-12-15 16:00:24 | checked on site airflow normal . Ahu running normal. no trip. cooling valve not control by BMS in auto mode. inform Honeywell to check . | [8 empty] | FRC | Aircon very warm, AHU 11,2 not working -satha-low
FID4460 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 7 > Day Surgery |  | 2021-12-15 13:19:10 | 2021-12-15 14:46:01 | 2021-12-15 14:46:25 | 2021-12-15 14:46:46 | 2021-12-15 14:47:08 | 2021-12-15 14:47:36 | Cleared the basin choke | [8 empty] | Su | Basin choke -nazri-low
FID4458 | Electrical | Call System | Other: Alarm | Localised to room | RMG > RH > 7 > OT |  | 2021-12-15 12:02:15 | 2021-12-15 12:06:49 | 2021-12-15 12:12:40 | 2021-12-15 12:12:58 | 2021-12-15 12:13:16 | 2021-12-15 12:20:59 | Reset the call bell back to normal. | [8 empty] | Su | Call bell keep alarming -mani-low
FID4457 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1076 -1079 (4 Bed) |  | 2021-12-15 11:59:05 | 2021-12-15 12:02:42 | 2021-12-15 12:03:23 | 2021-12-15 12:03:43 | 2021-12-15 12:04:03 | 2021-12-15 12:08:42 | Adjusted VAV 1-2-3 temperature setpoint from 20c to 24c in bms system make it warm. Damper automatically close from 90% to 20%. | [8 empty] | FRC | Aircon make it warm -su-low
FID4456 | Medical Equipment | Medical Gas | Other: CO2 cylinder | Localised to room | RMG > RH > 7 > OT |  | 2021-12-15 11:47:14 | 2021-12-15 11:52:07 | 2021-12-15 12:09:06 | 2021-12-15 12:10:17 | 2021-12-15 12:10:39 | 2021-12-15 12:11:06 | delivered cylinder | [8 empty] | Su | Need to replace 2 big CO2 cylinder -mingcai-medium